## SITE
REF: | ITB
Lot: | x | Solid biomass heating system in the gymnasium of Garbova village, Ocnita district
Site: | y
Consolidated price list |  |  |  | Estimated amount in USD, 0 rate VAT
Cost Component / Section
1 | Territory development |  |  | 0
2 | Thermomecanics |  |  | 0
3 | Solar hot water system |  |  | 0
4 | Heating and ventilation |  |  | 0
5 | General construction works |  |  | 0
6 | Electricity and lighting |  |  | 0
7 | Automated control and regulation system |  |  | 0
8 | Water and sewage |  |  | 0
9 | Anti fire system |  |  | 0
10 | Fuel system |  |  | 0
11 | Commissioning |  |  | 0
12 | Service and Maintenance works for 3-years of operation |  |  | 0
| Total price of works |  |  | 0
No | Parameter |  | Unit | Value
1 | Annual heat consumption |  | MWh | 487.56
2 | Boiler efficiency at nominal output |  | percentage | 0%
3 | Annual fuel demand |  | MWh
4 | Net calorific value of the fuel |  | MJ/ton | 15000
5 | Net calorific value of the fuel |  | MWh/ton | 4.1667
6 | Annual fuel consumption |  | ton
7 | Estimated fuel price |  | USD/ton | 110
8 | Annual cost of fuel |  | USD
9 | Discount rate |  | percentage | 10%
10 | Expected lifetime of the boiler |  | years | 10
11 | Current value (VC) of fuel |  | USD
Total cost of life-cycle (Price of works + VC fuel) |  |  | USD
Bidder: |  |  | Signature
No changes to the initial structure of this document are allowed. Any modifications made in the document, may result in Bidder's disqualification.

## TA
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solid biomass heating system in the gymnasium of Garbova village, Ocnita district
Site: | y
Section: |  | Territory development
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive ) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Construction works |  |  |  | 0
|  | Chapter 1.1.Cement-concrete platform |  |  |  | 0
1 | DA06B2 | Layer of cylindrical natural aggregates, having the resistant function of filtering, isolation , ventilation, anti-freeze and proof course, with mechanical laying, with sand | m3 | 4.1 |  | 0
2 | DA06B1 | Layer of cylindrical natural aggregates, having the resistant function of filtering, isolation , ventilation, anti-freeze and proof course, with mechanical laying, with ballast | m3 | 4.1 |  | 0
3 | CG22A | Plain concrete flooring class C 10/8 (Bc 10/B 150) thickness 10 cm, in continuous surface, primed, poured on site, in rooms with surface bigger than 16 sqm (B25 (F200), gr.8 cm) | m2 | 41 |  | 0
4 | DE11A | Small curbs, ready-made from concrete with section 10x15 cm, to delimitate green areas, sidewalks, alleys, etc., placed on concrete foundation B-15, БР 100.20.8 | m | 26 |  | 0
|  | Chapter 1.2. Welded panels (Eurofence) - 30,40 m |  |  |  | 0
5 | CO06B correct | Fencing wire mesh with fence panels made of round steel frame fixed on ready-made reinforced concrete pillars mounted at 2 m distance from each other, interaxed by tamping the ballast, the ridge height of 1,80 m ("GARDLAIN") | m | 30.4 |  | 0
6 | CA03F | Plain concrete poured with classical means in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according art. CA01, poured with classical means, plain concrete class В15 | m3 | 0.64 |  | 0
|  | Chapter 1.3. Gate "STANDART" l=1,0m, Н=1,8m (1 unit) |  |  |  | 0
7 | CK14A | Metallic gates with frames made of round steel profiles, ready-made, including the accessories necessary, mounted on reinforced concrete poles, gate "STANDART" code 6204 | m2 | 1.8 |  | 0
|  | Chapter 1.4. Metallic fence (11,0 m) |  |  |  | 0
8 | TsA02A | Manual digging of soil in limited spaces, under 1,00 m or over 1,00 m in width, executed without support, with vertical slope, in foundations, channels, drainages, twinning steps, in non-cohesive soil or lightly cohesive soil depth < 0,75 m light soil | m3 | 2.6 |  | 0
9 | TsD01B | Scattering with shovel of loose soil, in uniform layers, of 10-30 cm thickness, with a throw of up to 3 m from piles, including smashing the clods, soil from middle ground | m3 | 1.45 |  | 0
10 | TsD04B | Manual punning of piles made in horizontal or inclined digging at 1/4, including watering each soil layer in part with 10 cm thickness of cohesive soil | m3 | 1.45 |  | 0
11 | CO07C correct | Metallic fence of metal and tin frames of 1 mm thickness | kg | 457.1 |  | 0
14 | CA03F | Plain concrete poured with classical means in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according art. CA01, poured with classical means, plain concrete class В15 | m3 | 1.04 |  | 0
15 | TsC54B | Crushed stone foundation layer | m3 | 0.16 |  | 0
16 | CB02A | Boxes from reusable panels, with boarding from short and super short wood planks to pour the concrete in forms, glass-shaped foundations and equipment platforms including support | m2 | 10.24 |  | 0
|  | Chapter 1.5. Metallic gate |  |  |  | 0
17 | CO07C correct | Metallic fence of metal and tin frames of 1 mm thickness | kg | 27.95 |  | 0
18 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment | t | 0.03 |  | 0
19 | IzD04A | Painting the articles and metallic constructions with oil paint in 2 layers, executed from profiles, of 8mm-12mm thickness inclusive , with hand brush | t | 0.03 |  | 0
|  | Chapter 1.7. Steel ash container Dn=0,6m, H=1,0m with lid -(6 units) |  |  |  | 0
23 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, all or partially embedded in concrete | kg | 336 |  | 0
24 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment. | t | 0.336 |  | 0
25 | IzD04A | Painting the articles and metallic constructions with oil paint in 2 layers, executed from profiles, between 8mm-12mm thickness inclusive , with hand brush | t | 0.336 |  | 0
|  | Chapter 2. Equipment |  |  |  | 0
26 |  | Wheelbarrow with steel clamp, Vclamp =0,1m3 | un | 1 |  | 0
|  | Removing fertile soil |  |  |  | 0
27 | TsA02A | Manual digging of soil in limited spaces, under 1,00 m or over 1,00 m in width, executed without support, with vertical slope, in foundations, channels, drainages, twinning steps, in non-cohesive soil or lightly cohesive soil depth < 0,75 m light soil | m3 | 7 |  | 0
28 | RpCU09A | Manual transportation with wheelbarrow with rubber wheel at 100 m distance, the load of 100 - 120 kg, including setting the circulation cabinets and cleaning the rails of wheelbarrow by loading and unloading through settlement | t | 8.4 |  | 0
|  | Vertical systematization |  |  |  | 0
29 | TsA02B | Manual digging of soil in limited spaces, under 1,00 m or over 1,00 m in width, executed without support, with vertical slope, in foundations, channels, drainages, twinning steps, in non-cohesive soil or lightly cohesive soil depth < 0,75 m middle ground | m3 | 12 |  | 0
30 | RpCU09A | Manual transportation with wheelbarrow with rubber wheel at 100 m distance, the load of 100 - 120 kg, including setting the circulation cabinets and cleaning the rails of wheelbarrow by loading and unloading through settlement | t | 19.2 |  | 0
31 | TsD05B | Mechanical compacting with rammer of 150-200 kg of piles in successive layers of 20-30 cm thickness, excluding watering each layer in part, filling made of cohesive soil | 100 m3 | 0.12 |  | 0
|  | Demolition of buildings and installations |  |  |  | 0
32 | TsH02B | Manual tree felling by consecutive removing the branches, and trunk 11-30 cm | unit | 1 |  | 0
33 | TsH21A | Mechanical extraction of trees with diameter up to 10 cm, with earth ballot at roots, without covering the crown and by packing the ballot with wire mesh | unit | 1 |  | 0
Total VAT 0 rate | [5 empty] | 0

## TM
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solid biomass heating system in the gymnasium of Garbova village, Ocnita district
Site: | y
Section: |  | Thermomecanics
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive ) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Assembling works |  |  |  | 0
1 | IA14C | Monobloc steel heating boiler (hot water 90/70 degrees) with calorific power 150 kW with solid biomass - pellets, with build-in control panel, productivity min 80%, Рnom = 1,5 bar, class 3, ЕN 303-5 | unit | 1 |  | 0
2 | IA14B | Monobloc steel heating boiler (hot water 90/70 degrees), with calorific power 100 kW with solid biomass - pellets, with build-in control panel, productivity min 80%, Рnom = 1,5 bar, class 3, ЕN 303-5 | unit | 1 |  | 0
3 | IA38B | Circulating (recirculating) pump mounted on existing pipe, by flanges, with diameter over 2" | unit | 4 |  | 0
4 | IA28A | Expending vessel, mounted on platform having the capacity V=500 l | unit | 1 |  | 0
5 | IA25A | Pipe sludge separator, in central heating system, with nominal entering diameter 80 mm (dirt trap) | unit | 1 |  | 0
6 | IA38B | Circulating (recirculating) pump mounted on existing pipe, by flanges, with diameter over 2" | unit | 2 |  | 0
7 | IA23A | Liquid fuel filter , Dn20 mm | unit | 1 |  | 0
8 | IA38B | Circulating (recirculating) pump mounted on existing pipe, by flanges, with diameter over 2" | unit | 2 |  | 0
9 | IA17D | Vertical boiler mounted on floor, boiler having the capacity 3000 l (storage tank for heating system ) | unit | 1 |  | 0
10 | IA25A | Pipe sludge separator, in central heating system, with nominal entering diameter 20 mm (dirt trap) | unit | 2 |  | 0
11 | IA27B | Condenser reservoir, mounted on platform having the capacity 1000 l | unit | 1 |  | 0
12 | IA39A | Water softening installation, fully equiped, with water flow of 900 -2250 l/h (Decalux-10 ET 500 or similar) | unit | 1 |  | 0
13 | ID03B | Three-way plug valve with flanges with stuffing, for central heating installations, with nominal diameter 40 mm (three-way plug valve VF3) | unit | 1 |  | 0
14 | SE58A | Cold and hot water meters, with diameter -40 mm (calorific power measuring meter "Hydrometer") | unit | 1 |  | 0
|  | Chapter 2. Sanitary works |  |  |  | 0
15 | IzH05B | Pipe insulation with glass wool mattresses, mineral wool type I or type P stitched on one side, on weave of galvanized wire, made on site, having the thickness 60 mm, on pipes with circumference over thermal insulation more than 35 cm (mineral-cotton slabs with synthetic binder brand 75) | m2 | 13.1 |  | 0
16 | IzI09A1 | Protection of thermal insulation of black tin or galvanized pipes of 0,5 mm thickness screwed with round slot, self-tapping screws, having the circumference of pipe over thermal insulation between 0,90 and 1,6 m, manufacturing | m2 | 13.3 |  | 0
17 | IzI09A2 | Protection of thermal insulation of black tin or galvanized pipes of 0,5 mm thickness screwed with round slot, self-tapping screws, having the circumference of pipe over thermal insulation between 0,90 and 1,6 m, assembling | m2 | 13.3 |  | 0
18 | IzH40B | Insulation with perforated fiberglass cloth brand "ХПС-Т-5" of pipes of diameter more than 25 mm | m2 | 1.27 |  | 0
19 | IzI09A1 | Protection of thermal insulation of black tin or galvanized pipes of 0,5 mm thickness screwed with round slot, self-tapping screws, having the circumference of pipe over thermal insulation between 0,90 and 1,6 m, manufacturing | m2 | 30.9 |  | 0
20 | IzI09A2 | Protection of thermal insulation of black tin or galvanized pipes of 0,5 mm thickness screwed with round slot, self-tapping screws, having the circumference of pipe over thermal insulation between 0,90 and 1,6 m, assembling | m2 | 30.9 |  | 0
21 | IzH05B | Pipe insulation with glass wool mattresses, mineral wool type I or type P stitched on one side, on weave of galvanized wire, made on site, having the thickness 40 mm, on pipes with circumference over thermal insulation more than 35 cm (mineral-cotton mats stitched in metal gauze lining type m2 brand 125) | m2 | 21.94 |  | 0
22 | IzI09A1 | Protection of thermal insulation of black tin or galvanized pipes of 0,5 mm thickness screwed with round slot, self-tapping screws, having the circumference of pipe over thermal insulation between 0,90 and 1,6 m, manufacturing | m2 | 22.6 |  | 0
23 | IzI09A2 | Protection of thermal insulation of black tin or galvanized pipes of 0,5 mm thickness screwed with round slot, self-tapping screws, having the circumference of pipe over thermal insulation between 0,90 and 1,6 m, assembling | m2 | 22.6 |  | 0
24 | CL16B | Thick sheet metal lining (silo funnels, chimney flues, tanks and troughs) in chimney flues (chimney flues) | t | 0.398 |  | 0
25 | IA18J | Fine fitting for central heating boilers: faucet control valve for fittings (for thermometer ЗКh-1-87) | unit | 7 |  | 0
26 | IA18J | Fine fitting for central heating boilers: faucet control valve for fittings (to measure pressure ЗКh-275.00.90) | unit | 19 |  | 0
27 | IA18J | Fine fitting for central heating boilers: faucet control valve for fittings (to measure pressure ЗКh-287.00.90) | unit | 12 |  | 0
28 | IA18J | Fine fitting for central heating boilers: faucet control valve for fittings (to measure level ЗКh-223-89) | unit | 2 |  | 0
29 | IA18J | Fine fitting for central heating boilers: faucet control valve for fittings (to measure temperature ЗКh-2-87) | unit | 7 |  | 0
30 | ID04E | Stop or retention valve with joints for central heating installations with nominal diameter 80 mm (ball valve JIP Standart FF "Danfoss") | unit | 2 |  | 0
31 | ID04F | Stop or retention valve with joints for central heating installations with nominal diameter 80 mm (butterfly valve SYLAX (VFY-WH)) | unit | 14 |  | 0
32 | ID04D | Stop or retention valve with joints for central heating installations with nominal diameter 65 mm (butterfly valve SYLAX (VFY-WH)) | unit | 4 |  | 0
33 | ID04B | Stop or retention valve with joints for central heating installations with nominal diameter 40 mm (butterfly valve SYLAX (VFY-WH)) | unit | 2 |  | 0
34 | ID04B | Stop or retention valve with joints for central heating installations with nominal diameter 32 mm (butterfly valve SYLAX (VFY-WH)) | unit | 2 |  | 0
35 | ID04A | Stop or retention valve with joints for central heating installations with nominal diameter 25 mm (butterfly valve SYLAX (VFY-WH)) | unit | 4 |  | 0
36 | ID04A | Stop or retention valve with joints for central heating installations with nominal diameter 20 mm (full-opening ball valve type BVR UNI ISO 7/1) | unit | 11 |  | 0
37 | ID04E | Stop or retention valve with joints for central heating installations with nominal diameter 80 mm (flange stop ball valve type NVD402 "Danfoss") | unit | 4 |  | 0
38 | ID04B | Stop or retention valve with joints for central heating installations with nominal diameter 40 mm (stop ball valve type 223 "Danfoss") | unit | 1 |  | 0
39 | ID04B | Stop or retention valve with joints for central heating installations with nominal diameter 32 mm (stop ball valve type 223 "Danfoss") | unit | 1 |  | 0
40 | ID04A | Stop or retention valve with joints for central heating installations with nominal diameter 20 mm (stop ball valve type 223 "Danfoss") | unit | 2 |  | 0
41 | ID04B | Stop or retention valve with joints for central heating installations with nominal diameter 40 mm (safety valve, flange lifting 17с29нж) | unit | 1 |  | 0
42 | ID04A | Stop or retention valve with joints for central heating installations with nominal diameter 20 mm (safety valve, flange lifting 17с29нж) | unit | 4 |  | 0
43 | ID06A | Air release valve with mobile key for central heating installations, with nominal diameter 10 mm (brass automatic air valve with threaded joining type MATIC company "Danfoss" VF3, 149 B5 106) | unit | 2 |  | 0
44 | ID06A | Air release valve with mobile key for central heating installations, with nominal diameter 10 mm (two-way safety valve Regulus DBV 1 3/4 Czech Rep) | unit | 2 |  | 0
45 | IC12D | Seamless or longitudinally welded steel pipe for constructions, welded in distribution pipelines, in central heating installations in residential or social-cultural buildings, pipe with outer diameter and wall thickness 89 x 3,0 mm | m | 45 |  | 0
46 | IC12C | Seamless or longitudinal welded steel pipe for constructions, welded in distribution pipelines, in central heating installations in residential or social-cultural buildings , pipe with outer diameter and wall thickness 76 x 3,0 mm | m | 7 |  | 0
47 | IC12A | Seamless or longitudinal welded steel pipe for constructions, welded in distribution pipelines, in central heating installations in residential or social-cultural buildings , pipe with outer diameter and wall thickness 57 x 3,0 mm | m | 15 |  | 0
48 | IC11E | Longitudinally welded black steel pipe for installations, non-threaded, welded in columns, in central heating installations in residential or social-cultural buildings, pipe having the diameter 45 x 2,8 mm | m | 7 |  | 0
49 | IC11D | Longitudinally welded black steel pipe for installations, non-threaded, welded in columns, in central heating installations in residential or social-cultural buildings, pipe having the diameter 38x2,8 mm | m | 5 |  | 0
50 | IC11D | Longitudinally welded black steel pipe for installations, non-threaded, welded in columns, in central heating installations in residential or social-cultural buildings, pipe having the diameter 32x2,8 mm | m | 15 |  | 0
51 | IC11C | Longitudinally welded black steel pipe for installations, non-threaded, welded in columns, in central heating installations in residential or social-cultural buildings, pipe having the diameter 25x2,8 mm | m | 35 |  | 0
52 | IC11B | Longitudinally welded black steel pipe for installations, non-threaded, welded in columns, in central heating installations in residential or social-cultural buildings, pipe having the diameter 20х2,0 mm | m | 1 |  | 0
53 | IE03D | Perform tightness test procedure under pressure of feeding pipelines of heating devices (heaters, thermal convectors, plinth convectors, etc.) with diameter 80 x 3,5 ... 159 x 8 mm | m | 45 |  | 0
54 | IE03C | Perform tightness test procedure under pressure of feeding pipelines of heating devices (heaters, thermal convectors, plinth convectors, etc.) with diameter 54 x 3,5 ... 83 x 3,5 mm | m | 22 |  | 0
55 | IE03B | Perform tightness test procedure under pressure of feeding pipelines of heating devices (heaters, thermal convectors, plinth convectors, etc.) with diameter 1 1/4" ... 2" | m | 27 |  | 0
56 | IE03A | Perform tightness test procedure under pressure of feeding pipelines of heating devices (heaters, thermal convectors, plinth convectors, etc.) with diameter 3/8" ... 1" | m | 36 |  | 0
57 | IE04D | Perform expansion-contraction and running test of pipes in heating installations heaters, thermal convectors, plinth convectors, etc.) with diameter 89 x 3,5 ... 159 x 8 mm | m | 45 |  | 0
58 | IE04C | Perform expansion-contraction and running test of pipes in heating installations heaters, thermal convectors, plinth convectors, etc.) with diameter 54 x 3,5 ... 83 x 3,5 mm | m | 22 |  | 0
59 | IE04B | Perform expansion-contraction and running test of pipes in heating installations heaters, thermal convectors, plinth convectors, etc.) with diameter 1 1/4" ... 2" | m | 27 |  | 0
60 | IE04A | Perform expansion-contraction and running test of pipes in heating installations heaters, thermal convectors, plinth convectors, etc.) with diameter 3/8" ... 1" | m | 36 |  | 0
61 | IC42A | Supports and fasteners for support of pipes, boilers, devices and recipients, having the weight less than 2 kg / unit | kg | 192.76 |  | 0
62 | VA05A | On-site assembling of ALP ventilation tubes, ready-made, having the section perimeter 450 mm (assembling the chimney) | m | 14 |  | 0
| Company price | Metal chimney with double tin walls made of stainless steel. Inner diameter 450 mm, H = 15,0 m, with thermal insulation - 50 mm, in set: |  |  |  | 0
63 |  | Stainless steel cone-shaped adaptor CF 450/520 | unit | 1 |  | 0
64 |  | Stainless steel wall clamp CFO-100 Д520 | unit | 6 |  | 0
65 |  | Stainless steel pipe CF L1000 Д450/520 | unit | 12 |  | 0
66 |  | Stainless steel condensation module CF Д450 | unit | 1 |  | 0
67 |  | Stainless steel lid module CF 87* Д520 | unit | 1 |  | 0
68 |  | Stainless steel tee CF 87* Д450/520 | unit | 1 |  | 0
|  | Chapter 3. Equipment |  |  |  | 0
69 |  | Monobloc steel heating boiler (hot water 90/70 degrees with calorific power 150 kW with solid biomass - pellets, with build-in control panel, productivity min 80%, Рnom = 1,5 bar, class 3, ЕН 303-5,2012 | unit | 1 |  | 0
70 |  | Monobloc steel heating boiler (hot water 90/70 degrees), with calorific power 100 kW with solid biomass - pellets, with build-in control panel, productivity min 80%, Рnom = 1,5 bar, class 3, ЕН 303-5,2012 | unit | 1 |  | 0
71 |  | Circulating (recirculating) pump mounted on existing pipe, by flanges, with diameter over 2" (outline No.1), productivity Qp=10,8m3/hour, pressure Нр=6,7 m.c.a., N=22 -464 W, class А, А 16-2 (ЕЕ1<0,2) | unit | 2 |  | 0
72 |  | Circulating (recirculating) pump mounted on existing pipe, by flanges, with diameter over 2" (outline No.2), productivity Qp=10,8m3/hour, pressure Нр=15 m.c.a., N=30 -1336 W, class А, А 16-2 (ЕЕ1<0,2) | unit | 2 |  | 0
73 |  | Expending vessel V=500 l, , P=6 bar, 41VE0150 or similar | unit | 1 |  | 0
74 |  | Pipe sludge separator, in central heating system, with nominal entering diameter 80 mm (dirt trap), Р 16 bar, 149В 1802 or similar | unit | 1 |  | 0
75 |  | Circulating (recirculating) pump mounted on existing pipe, by flanges, with diameter over 2" Qp=1,6 m3/hour; Нр-4,5 m.c.a. N=37-96 W, MX 12-2 or similar | unit | 2 |  | 0
76 |  | Proportional water dosing equipment - build-in bypass oxygen D 20 mm, (similar Dosaphos 250) | unit | 1 |  | 0
77 |  | Water circulation pump, mounted on existing pipe, by flanges, with diameter over 2" Qp=0,1 m3/hour, pressure Нр=21,5 m.c.a., N=0,3 кW, BM1-3 or similar | unit | 2 |  | 0
78 |  | Vertical boiler (buffer) for heating system V=3000 L, Ру 8 bar | unit | 1 |  | 0
79 |  | Pipe sludge separator, in central heating system, with nominal entering diameter 20 mm (dirt trap), Р 16 bar, 149В 1769 or similar | unit | 2 |  | 0
80 |  | Vessel for additional water, V=1000 L | unit | 1 |  | 0
81 |  | Water softening installation, fully equipped, with water flow of 900 -2250 l/h (Decalux-5 ET 500 or similar) | unit | 1 |  | 0
82 |  | Universal carrying trolley V=0,1 m3 | unit | 1 |  | 0
83 |  | Three-way plug valve with flanges with stuffing, for central heating installations, with nominal diameter 40 mm, "Danfoss or similar" | unit | 1 |  | 0
84 |  | Heat meter D 40 mm, "Hydrometer" Sharky 775, h50-15), EN 1434 | unit | 1 |  | 0
Total VAT 0 rate | [5 empty] | 0

## TMS
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solid biomass heating system in the gymnasium of Garbova village, Ocnita district
Site: | y
Section: |  | Solar hot water system
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive ) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
0
0
Total VAT 0 rate | [5 empty] | 0

## HV
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solid biomass heating system in the gymnasium of Garbova village, Ocnita district
Site: | y
Section: |  | Heating and ventilation
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive ) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Heating |  |  |  | 0
1 | IB06C | Steel radiators, monobloc with length of 1501 - 2000 mm ("Korado" type 33 1600х600(h)or similar) | unit | 1 |  | 0
2 | ID06A | Air release valve with mobile key for central heating installations, with nominal diameter 1/2" (corner locking valve RLV-15) | unit | 2 |  | 0
3 | ID06A | Air release valve with mobile key for central heating installations, with nominal diameter 1/2" (air valve for radiator) | unit | 1 |  | 0
4 |  | Keys for air inlets R74Y001 | unit | 1 |  | 0
5 | ID04A | Stop or retention valve with joints for central heating installations with nominal diameter 15 mm (ball valve with drain Giacomini) | unit | 2 |  | 0
6 | IC13A | Longitudinally welded black steel pipe, for installations, with thread and socket mounted by screwing the connections to devices in central heating installations, pipe with diameter 20x2,0 mm (welded) | m | 10 |  | 0
7 | IE03A | Perform tightness test procedure under pressure of feeding pipelines of heating devices (heaters, thermal convectors, plinth convectors, etc.) with diameter 3/8" ... 1" | m | 10 |  | 0
8 | IE04A | Perform expansion-contraction and running test of pipes in heating installations heaters, thermal convectors, plinth convectors, etc.) with diameter 3/8" ... 1" | m | 10 |  | 0
9 | IzJ09B | Painting the tin cover of pipes and devices with 2 layer oil paint, including priming | m2 | 1.3 |  | 0
10 | AcE51A | Connection to existing steel pipeline (with connecting pipes) with the diameter of connecting pipes 15 mm | part | 2 |  | 0
|  | Ventilation |  |  |  | 0
11 | VA02A | Manufacturing and mounting of straight ventilation channels, of galvanized steel or aluminium 0,3 - 2 mm thickness, having the perimeter of rectangular section 250 - 700 mm (gr.0,6 mm) | m2 | 2.64 |  | 0
12 | VB27A | Protective lid for circular manholes with perimeter 230 - 700 mm (umbrella ЗKц Д280) | unit | 1 |  | 0
13 | CC09B | Mounting rabbit mesh to support plaster ceiling , walls, protection of thermal insulators, masking of pipes, applied on straight ceilings, on steel - concrete D = 6-8 mm, with eyelids 26-35 mm inclusiv | m2 | 0.2 |  | 0
14 | IzH05B | Pipe insulation with glass wool mattresses, mineral wool type I or type P stitched on one side, on weave of galvanized wire, made on site, having the thickness20; 30; 40; 50 or 60 mm, on pipes with circumference over thermal insulation more than 30 mm (fiber optic mat, covered with armored aluminium foil 50 mm thick ISOVER-KIM-AL) | m2 | 3.8 |  | 0
15 |  | Adhesive band for sealing the joints ISOVER AL-TEPPI | m | 15 |  | 0
16 | CL20A | Ventilation grilles ready-made of black sheet, with manually adjustable blinds, painted and embedded in masonry (still air flowing grid SKP 500х400h) | unit | 1 |  | 0
|  | Thermal network |  |  |  | 0
17 | TsC03B1 | Mechanic digging with excavator of 0,40-0,70 mc with internal combustion motor and hydraulic control, in soil with natural humidity, unloading in vehicles on ground category II | 100 m3 | 0.76 |  | 0
18 | TsA20B | Manual digging of soil, in slopes, in channels cut by excavator or scraper, to fill the digging in slope profile, in middle ground | m3 | 2.4 |  | 0
19 | TsD02A1 | Scattering loose soil extracted from ground category I or II, by bulldozer tractor on tracks 65-80 CP, in layers of 15-20 cm | 100 m3 | 0.43 |  | 0
20 | TsD05A | Mechanical compacting with rammer of 150-200 kg of piles in successive layers of 20-30 cm with tin sheets of , excluding watering each layer in part, filling made of cohesive soil | 100 m3 | 0.43 |  | 0
21 | TsD01B | Scattering with shovel of loose soil, in uniform layers, of 10-30 cm with tin sheets of , with a throw of up to 3 m from piles, including smashing the clods, soil from middle ground | m3 | 10.7 |  | 0
22 | TsD04B | Manual punning of piles executed in horizontal or inclined digging at 1/4, including watering each layer of ground in part, having 10 cm thickness cohesive soil | m3 | 10.7 |  | 0
|  | Underground laying of pipes |  |  |  | 0
23 | TfA01B2 | Steel pipe installed in trench, 1-3 m deep or on the ground at the height between 3-15m, including cold pressure testing, tightness testing and complex testing with circulating fluids, having the diameter 89x3,0 mm | m | 40 |  | 0
24 | TfA01A2 | Steel pipe installed in trench, 1-3 m deep or on the ground at the height between 3-15m, including cold pressure testing, tightness testing and complex testing with circulating fluids, having the diameter 45х2,0 mm | m | 30 |  | 0
25 | TfA01A2 | Steel pipe installed in trench, 1-3 m deep or on the ground at the height between 3-15m , including cold pressure testing, tightness testing and complex testing with circulating fluids, having the diameter 38х2,0 mm | m | 36 |  | 0
26 | TfA01A2 | Steel pipe installed in trench, 1-3 m deep or on the ground at the height between 3-15m , including cold pressure testing, tightness testing and complex testing with circulating fluids, having the diameter 32х2,0 mm | m | 30 |  | 0
27 | TfA02B2 | Ready-made steel elbow pipe, installed in the pipeline in trench, 1-3 m deep or on the ground at the height between 3-15m , including cold pressure testing, tightness testing and complex testing with circulating fluids, having the diameter 89 mm (pipe bend 90') | unit | 6 |  | 0
28 | TfA02A2 | Ready-made steel elbow pipe, installed in the pipeline in trench, 1-3 m deep or on the ground at the height between 3-15m , including cold pressure testing, tightness testing and complex testing with circulating fluids, having the diameter 45 mm (bend 45') | unit | 4 |  | 0
29 | TfB02D2 | Assembling slide valve with vent or stop valve made of steel or iron up to Pn 40, in trench, 1-3 m deep or on the ground at the height between 3-15m m with nominal value Dn 80 mm (ball valve LD-WW) | unit | 2 |  | 0
30 | TfB02A2 | Assembling slide valve with vent or stop valve made of steel or iron up to Pn 40, in trench, 1-3 m deep or on the ground at the height between 3-15m with nominal value Dn 45 mm (ball valve LD-WW) | unit | 2 |  | 0
31 | TfB02A2 | Assembling slide valve with vent or stop valve made of steel or iron up to Pn 40, in trench, 1-3 m deep or on the ground at the height between 3-15m with nominal value Dn 25 mm (ball valve LD-WW) | unit | 6 |  | 0
32 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, fully or partially embedded in concrete | kg | 101.12 |  | 0
|  | Trench КЛ-90х45-8 (42 m) |  |  |  | 0
33 | TsC54A | Sand layer foundation | m3 | 4.12 |  | 0
34 | CP16A | Assembling L- or U-type elements made of reinforced concrete for trenches (thermal, heating, cables, etc.) hod Л4-8 | unit | 14 |  | 0
35 | CP16B | Assembling ready-made elements made of reinforced concrete for trenches (thermal, heating, cables, etc.), straight or curved plates П8-8 | unit | 14 |  | 0
36 | CP10B | Mount pre-cast elements from reinforced steel in residential and social-cultural buildings with monolith reinforced concrete structure, mixt or bearing masonry, at height up to 20 m inclusive with volume from 0,2-2,5 mc bearing block ОП-1 | unit | 24 |  | 0
37 | CP10B | Mount pre-cast elements from reinforced steel in residential and social-cultural buildings with monolith reinforced concrete structure, mixt or bearing masonry, at height up to 20 m inclusive with volume from 0,2-2,5 mc bearing block ОП-2 | unit | 8 |  | 0
38 | AcE51A | Connect to existing steel pipeline (with nozzle) having the diameter of nozzle 40x80 mm | piesa | 2 |  | 0
|  | Pipe hub УТ 1 |  |  |  | 0
|  | Thermal chamber ТК-1, 1,8х1,8х2,0(h) |  |  |  | 0
39 | CP50A | Mounting pre-cast concrete elements. Block-wall for basement, weight 0,5 t. Note: type of pre-cast element will be included as per project ФС-4-8м | unit | 30 |  | 0
40 | CP16B | Assembling ready-made elements made of reinforced concrete for trenches (thermal, heating, cables, etc.), straight or curved plates | unit | 1 |  | 0
41 | CA03F | Plain concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class.... B7,5 | m3 | 0.768 |  | 0
42 | AcE07A | Install steel or concrete steel lids on manholes of water and sewage systems, off road type I Т | unit | 2 |  | 0
43 | CP16B | Assembling ready-made elements made of reinforced concrete for trenches (thermal, heating, cables, etc.), straight or curved plates КЦО-1 | unit | 2 |  | 0
44 | CP16B | Assembling ready-made elements made of reinforced concrete for trenches (thermal, heating, cables, etc.), straight or curved plates КЦ-7-3 | unit | 2 |  | 0
45 | CL10C | Metallic stairs, landings, bridges, bars and constructions to support technological equipment or metallic platforms for large aggregates delivered in ready-made sub-sets, at heights up to 35 m, with weight up to 0,150 t, assembled by welding | t | 0.05 |  | 0
46 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment. | t | 0.05 |  | 0
47 | IzD04A | Painting metallic articles and constructions with oil paint in 2 layers, executed from profiles, between 8mm-12mm with inclusive, with hand brush | t | 0.05 |  | 0
48 | CA03G | Reinforced concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, reinforced concrete class... B7,5, drainage pit and ДП-1 | m3 | 2.8 |  | 0
|  | Pipe nozzle УТ 2 |  |  |  | 0
49 | CA03F | Plain concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class.... B15 | m3 | 0.8 |  | 0
50 | IC44C | Manufacturing, mounting and cementing protection pipe through walls, pipe having the diameter 133 x 4,0 mm (L=0,5 m) | unit | 2 |  | 0
51 | AcE51A | Connect to existing steel pipeline (with nozzle) having the diameter of nozzle 32x40 mm | piesa | 2 |  | 0
52 | IzH05B | Pipe insulation with glass wool mattresses, mineral wool type I or type P stitched on one side, on weave of galvanized wire, made on site, having the thickness 60 mm, on pipes with circumference over thermal insulation more than 35 cm (mineral-cotton slabs with synthetic binder brand 125 thickness 50mm) | m2 | 17.6 |  | 0
53 | IzH40B | Insulation with perforated fiberglass cloth brand "ХПС-Т-5" of pipes of diameter over 25 mm | m3 | 0.69 |  | 0
54 | IzI05B | Protection of thermal-insulation of pipes mde with bitumen type I A fiber glass mesh, tied with soft galvanised steel wire with diameter 1,25 mm РСТ | m2 | 50 |  | 0
55 | IzF04F k=2 | Hydro-insulated layer executed at temperature on terraces, roofs, or foundations on soils without underground waters, including mouldings of current hydro-insulation on inclined up to 40% or vertical, plane or curved surfaces, with bitumen or rubber bitumen applied with brush or rubber pump (purlin) 2 layers of cold bitumen | m2 | 30 |  | 0
|  | Drainage pit ДК1 |  |  |  | 0
56 | AcE13A | Executing the manholes from ready-made reinforced concrete elements, for water supply circular (ring) with diameter 1,0 m, in soil without underground water | m3 | 1.04 |  | 0
57 | AcE13A1 | Ready-made reinforced concrete elements for water supply circular (ring) with diameter 1,0 m, for sewage, in soil without underground water. Note: resource with 0,00 (zero) norm in accordance with the project | unit | 1 |  | 0
58 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment. | t | 0.03 |  | 0
59 | IzD04A | Painting metallic articles and constructions with oil paint in 2 layers, executed from profiles, between 8mm-12mm inclusive, with hand brush | t | 0.03 |  | 0
60 | CA02C | Plain concrete poured in equalizers, slopes at height up to 35 m inclusive, prepared by concrete mixer according to art. CA01 or commercial concrete, poured with classical means B7,5 | m3 | 0.45 |  | 0
61 | CA03F | Plain concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class.... B7,5 | m3 | 0.05 |  | 0
62 | AcA16B | Install asbestos cement tubes assembled with steel sockets with flanges with the length 3 m and diameter 150 mm | m | 3 |  | 0
63 | TfB01H1 | Assembling slide valve with vent or stop valve made of steel or iron up to Pn 25, in trench, at 1m depth or on the ground up to 3 m with nominal diameter Dn 150 mm (automatic stop valve) | unit | 1 |  | 0
|  | Mine ШО1, ШО2 (4 units) |  |  |  | 0
64 | CA03F | Plain concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class.... B15 | m3 | 5.2 |  | 0
65 | CA03F | Plain concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class.... B7,5 | m3 | 0.6 |  | 0
66 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, fully or partially embedded in concrete | kg | 78.76 |  | 0
67 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, fully or partially embedded in concrete | kg | 238.4 |  | 0
68 | DB16A | Asphalt concrete coat with small aggregates, executed at hot temperatures, in thickness de 2,5 cm manual laying | m2 | 6.08 |  | 0
69 | IzF04F | Hydro-insulated layer executed at high temperature on terraces, roofs, or foundations on soils without underground waters, including mouldings of current hydro-insulation on inclined up to 40% or vertical, plane or curved surfaces, with bitumen or rubber bitumen applied with brush or rubber pump (purlin) lacquer БТ-577 | m2 | 6.08 |  | 0
70 | CC02E | Concrete steel fittings OB 37 prepared in site workshop, with bar diameter up to 8 mm inclusive, for slabs , excluding constructions executed with sliding plates | kg | 7.48 |  | 0
71 | CC02F | Concrete steel fittings OB 37 prepared in site workshop, with bar diameter more than 8 mm including, for slabs, excluding constructions executed with sliding plates | kg | 84.48 |  | 0
|  | Nozzle "А" (8 units) |  |  |  | 0
72 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, fully or partially embedded in concrete | kg | 9.6 |  | 0
73 | CE05A | Covers from anticorrosive profiled tin, curled or wrinkled, fixed with clamps, executed with dual stitches, executed on surfaces wider than 40 sqm from profiled tin sheets of 0.4mm thickness, including execution of aprons, connection to chimneys etc. | m2 | 4.72 |  | 0
74 | IzF04F | Hydro-insulated layer executed at high temperature on terraces, roofs, or foundations on soils without underground waters, including mouldings of current hydro-insulation on inclined up to 40% or vertical, plane or curved surfaces, with bitumen or rubber bitumen applied with brush or rubber pump (purlin) lacquer | m2 | 0.68 |  | 0
|  | Aerial installation and pipe connection |  |  |  | 0
75 | TfA01B1 | Steel pipe installed in trench, up to 1 m deep or on the ground at up to 3 m height, including cold pressure testing, tightness testing and complex testing with circulating fluids, having the diameter 89x3,0 mm | m | 10 |  | 0
76 | TfA01A1 | Steel pipe installed in trench, up to 1 m deep or on the ground at up to 3 m height, including cold pressure testing, tightness testing and complex testing with circulating fluids, having the diameter 38x2,0 mm | m | 10 |  | 0
77 | TfA02B1 | Ready-made steel elbow pipe, installed in the pipeline in trench, up to 1 m deep or on the ground at up to 3 m height, including cold pressure testing, tightness testing and complex testing with circulating fluids, having the diameter 76 mm (bend) | unit | 6 |  | 0
78 | TfB02D2 | Assembling slide valve with vent or stop valve made of steel or iron up to Pn 40, in trench, 1-3 m deep or on the ground at the height between 3-15m m with nominal value Dn 80 mm (ball valve LD-WW) | unit | 2 |  | 0
79 | TfB02A2 | Assembling slide valve with vent or stop valve made of steel or iron up to Pn 40, in trench, 1-3 m deep or on the ground at the height between 3-15m with nominal value Dn 15 mm (ball valve LD-WW) | unit | 6 |  | 0
80 | IC44C | Manufacturing, mounting and cementing protection pipe through walls, pipe having the diameter 133 x 4,0 mm (L=0,5 m) | unit | 2 |  | 0
81 | IC44A | Manufacturing, mounting and cementing protection pipe through walls, pipe having the diameter 57х3,0 mm (L=0,5 m) | unit | 4 |  | 0
82 | AcE51B | Connect to existing steel pipeline (with nozzle) having the diameter of nozzle 80x125 mm | piesa | 2 |  | 0
83 | IC42A | Supports and fasteners for support of pipes, boilers, devices and recipients, having the weight less than 2 kg / unit | kg | 10 |  | 0
84 | IzH40B | Insulation with perforated fiberglass cloth brand "ХПС-Т-5" of pipes of diameter over 25 mm | m3 | 0.1 |  | 0
85 | IzH05B | Pipe insulation with glass wool mattresses, mineral wool type I or type P stitched on one side, on weave of galvanized wire, made on site, having the thickness 60 mm, on pipes with circumference over thermal insulation more than 35 cm (mineral-cotton slabs with synthetic binder brand 125 thickness 50mm) | m2 | 4.4 |  | 0
86 | IzI09A1 | Protection of thermal insulation of black tin or galvanized pipes of 0,5 mm thickness screwed with round slot, self-tapping screws, having the circumference of pipe over thermal insulation between 0,90 and 1,6 m, manufacturing | m2 | 9.8 |  | 0
87 | IzI09A2 | Protection of thermal insulation of black tin or galvanized pipes of 0,5 mm thickness screwed with round slot, self-tapping screws, having the circumference of pipe over thermal insulation between 0,90 and 1,6 m, assembling | m2 | 9.8 |  | 0
|  | Dismantling and redo the asphaltic concrete coat |  |  |  | 0
88 | DG05A k=3 | Dismantle the coat up to 3 cm thickness, formed of permanent asphaltic coats, asphaltic concrete | m2 | 6 |  | 0
89 | DG01A | Dismantle the pavements or stone foundations on sand | m2 | 6 |  | 0
90 | TsC54A | Sand layer foundation | m3 | 0.9 |  | 0
91 | TsC54B | Crushed stone foundation layer | m3 | 0.9 |  | 0
92 | DB16D k=2,5 | Asphalt concrete coat with small aggregates, executed at hot temperatures, in thickness de 4 cm manual laying (10 cm thick) | m2 | 6 |  | 0
Total VAT 0 rate | [5 empty] | 0

## GCW
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solid biomass heating system in the gymnasium of Garbova village, Ocnita district
Site: | y
Section: |  | General construction works
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive ) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Digging works |  |  |  | 0
1 | TsA02E | Manual digging of soil in limited spaces, under 1,00 m or over 1,00 m in width, executed without support, with vertical slope, in foundations, channels, drainages, twinning steps, in middle or very cohesive soil depth < 1,5 m middle ground | m3 | 25.3 |  | 0
2 | TsD01B | Scattering with shovel of loose soil, in uniform layers, of 10-30 cm thickness, with a throw of up to 3 m from piles, including smashing the clods, soil from middle ground | m3 | 13.55 |  | 0
3 | TsD04B | Manual punning of piles made in horizontal or inclined digging at 1/4, including watering each soil layer in part with 10 cm thickness of cohesive soil | m3 | 13.55 |  | 0
|  | Chapter 2. Foundation |  |  |  | 0
4 |  | Foundation Фm1, Фm2 |  |  |  | 0
5 | CA02C | Plain concrete poured in equalizers, slopes, curves at height up to 35m inclusive , prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means B3,5 | m3 | 0.6 |  | 0
6 | CA03G | Reinforced concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class... В15 | m3 | 1.89 |  | 0
7 | CC01C | Concrete steel fittings OB 37 prepared in site workshop, with bar diameter up to 8 mm inclusive in isolated foundations | kg | 12.9 |  | 0
8 | CC01D | Concrete steel fittings OB 37 prepared in site workshop, with bar diameterover 8 mm inclusive in isolated foundations | kg | 51 |  | 0
9 | CB02A | Boxes from reusable panels, with boarding from short and super short wood planks to pour the concrete in forms, glass-shaped foundations and equipment platforms including support | m2 | 14.05 |  | 0
10 | CA03F | Plain concrete poured with classical means in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according art. CA01, poured with classical means, plain concrete class.... B15 | m3 | 0.6 |  | 0
11 |  | Fundament beams ФБm1 ... ФБm5 |  |  |  | 0
12 | TsC54A | Sand foundation layer | m3 | 4.3 |  | 0
13 | CA03G | Reinforced concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class... В15 | m3 | 2.97 |  | 0
14 | CC01E | Concrete steel fittings OB 37 prepared in site workshop, with bar diameter up to 8 mm inclusive in continuous foundations and radiation | kg | 42.8 |  | 0
15 | CC01F | Concrete steel fittings OB 37 prepared in site workshop, with bar diameterover 8 mm inclusive in continuous foundations and radiation | kg | 104.4 |  | 0
16 | CB02A | Boxes from reusable panels, with boarding from short and super short wood planks to pour the concrete in forms, glass-shaped foundations and equipment platforms including support | m2 | 22.85 |  | 0
17 | CA03F | Plain concrete poured with classical means in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according art. CA01, poured with classical means, plain concrete class.... B15 | m3 | 0.3 |  | 0
18 | IzF50A | Hydro insulation made from liquid glass cement mortar in foundations and walls applied on horizontal surfaces | m2 | 6.05 |  | 0
|  | Chapter 3. Body |  |  |  | 0
19 | CG01A | Support layer for flooring executed from cement mortar M 150-T of 3 cm thickness with finely plastered surface (5 cm thick) | m2 | 1.43 |  | 0
20 | CG01A1 k=4 | Support layer for flooring executed from cement mortar M 150-T of 3 cm thickness with finely plastered surface. The difference for each 0,5 cm of support layer of mortar M 150-T, should be added or deducted | m2 | 1.43 |  | 0
21 | CL08A | Metallic elements (pillars, beams, poles), ready-made, delivered fully assembled, mounted on site, in light construction structure | t | 2.435 |  | 0
22 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment. | t | 2.435 |  | 0
23 | IzD04A | Painting the articles and metallic constructions with oil paint in 2 layers, executed from profiles, between 8mm-12mm thickness inclusive , with hand brush | t | 2.435 |  | 0
|  | Chapter 4. Wall |  |  |  | 0
24 | CD73A | Light panel walls made of threaded tin with thermal insulation, Sandwich type, mounted on metallic or reinforced concrete ruler height under 12 m: in front of rulers. Note: * brand and type of panel tightness is determined by the project (stone wool 100 mm thick) | m2 | 112 |  | 0
|  | Chapter 5. Roof |  |  |  | 0
25 | CE44A | Light panel walls made of threaded tin with thermal insulation, Sandwich type, mounted on metallic ruler. Note: * brand and type of panel tightness is determined by the project. (stone wool 100 mm thick) | m2 | 55 |  | 0
26 | CE20A | Brass gutter systems made of anticorrosive tin Dn100 mm | m | 16 |  | 0
27 | CE22A | Brass drainpipe systems made of anticorrosive tin Dn100 mm | m | 14.4 |  | 0
28 | CE05B | Covers from anticorrosive profiled or galvanized tin, fixed with clamps, made of double clips in both ways, executed on surfaces wider than 40 mp with tin sheets 0,5 mm thickness, inclusive execution of aprons, beams, connection to chimneys etc. (0,8 mm thick) | m2 | 52 |  | 0
|  | Canopy К-1 |  |  |  | 0
29 | CL08A | Metallic elements (pillars, beams, poles), ready-made, delivered fully assembled, mounted on site, in light construction structure | t | 0.03 |  | 0
30 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment. | t | 0.03 |  | 0
31 | IzD04A | Painting the articles and metallic constructions with oil paint in 2 layers, executed from profiles, between 8mm-12mm thickness inclusive , with hand brush | t | 0.03 |  | 0
32 | CE06A | Covers from anticorrosive profiled tin, curled or wrinkled, mounted on metallic panels, executed on surfaces wider than 40 mp with profiled tin sheets connected with special clips or mechanical screws, of superior flange , including execution of aprons, beams, connection to chimneys etc. (profiled tin "LIDER" ЛК-20) | m2 | 3 |  | 0
|  | Chapter 6. Windows and doors |  |  |  | 0
33 | CK57C | Mounting PVC profiles: tilted (inclined, swing-out) with gap surface under 2 m2 in one frame (ОК1) | m2 | 0.96 |  | 0
34 | CK57D | Install PVS windows: tilted (inclined, swing-out) with gap surface under 2 m2 in one frame (ОК2) | m2 | 2.14 |  | 0
35 | CK12D | Metallic doors made from laminated steel profile, steel profiles prepared at cold temperatures, including fittings and accessories necessary to doors mounted in masonry of any nature in constructions with height up to 35 m including in 2 frames, with sheath surface up to 7 sqm inclusive (ИД-1) | m2 | 3.01 |  | 0
36 | CN20B | Internal or external painting on metallic carpentry with alkyd enamel in 2 layers including priming | m2 | 6.62 |  | 0
|  | Chapter 7. Floors |  |  |  | 0
37 | TsC53B | Compacting the ground with broken stone | 100m2 | 0.44 |  | 0
38 | CG22A | Plain concrete floors class C 10/8 (Bc 7,5/B 100) in 10 cm thick, in continuous surface, plastered, poured on site, in rooms with surface larger than 16 sqm (8 cm thick) | m2 | 44 |  | 0
39 | IzF03A1 | Anti-vapour barrier executed on horizontal surfaces with a layer of bitumen cardboard, glued on the entire surface with bitumen membrane (bitumen membrane) | m2 | 44 |  | 0
40 | CG01A | Support layer for flooring executed from cement mortar M 150-T of 3 cm thickness with finely plastered surface (2 cm thick) | m2 | 44 |  | 0
41 | CG17D | Flooring from ceramic tiles including supporting layer of adhesive mortar, executed on surfaces: larger than 16 m2 (13 mm thick) | m2 | 44 |  | 0
|  | Chapter 8. Other works |  |  |  | 0
|  | Chapter 8.1. External stairs and ramp |  |  |  | 0
42 | TsA02B | Manual digging of soil in limited spaces, under 1,00 m or over 1,00 m in width, executed without support, with vertical slope, in foundations, channels, drainages, twinning steps, in non-cohesive soil or lightly cohesive soil depth < 0,75 m middle ground | m3 | 2.2 |  | 0
43 | TsD01B | Scattering with shovel of loose soil, in uniform layers, of 10-30 cm thickness, with a throw of up to 3 m from piles, including smashing the clods, soil from middle ground | m3 | 0.86 |  | 0
44 | TsD04B | Manual punning of piles made in horizontal or inclined digging at 1/4, including watering each soil layer in part with 10 cm thickness of cohesive soil | m3 | 0.86 |  | 0
45 | TsC54B | Crushed stone foundation layer | m3 | 0.1 |  | 0
46 | CA03F | Plain concrete poured with classical means in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according art. CA01, poured with classical means, plain concrete class.... B7,5 | m3 | 2.55 |  | 0
47 | CB02A | Boxes from reusable panels, with boarding from short and super short wood planks to pour the concrete in forms, glass-shaped foundations and equipment platforms including support | m2 | 17.5 |  | 0
48 | CG22A1 | Plain concrete floors class C 10/8 (Bc 7,5/B 100) in 10 cm thick, in continuous surface, plastered, poured on site, in rooms with surface less or equal to 16 mp (В15, 2 cm thick) | m2 | 4.7 |  | 0
|  | Chapter 8.2. Metallic platform Пm1 (1 unit) |  |  |  | 0
49 | CL10C | Metallic stairs, landings, bridges, bars and constructions to support technological equipment or metallic platforms for large aggregates delivered in ready-made sub-sets, at height up to 35 m, with weight up to 0,150 t, assembled by way of welding | t | 0.26 |  | 0
50 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment. | t | 0.26 |  | 0
51 | IzD04A | Painting metallic articles and constructions with oil paint in 3 layers, executed from profiles with thickness between 8mm and 12mm inclusive, with hand brush | t | 0.26 |  | 0
|  | Chapter 8.3. Stall Л1 |  |  |  | 0
52 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, all or partially embedded in concrete | kg | 77.4 |  | 0
53 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment. | t | 0.08 |  | 0
54 | IzD04A | Painting the articles and metallic constructions with oil paint in 2 layers, executed from profiles, between 8mm-12mm thickness inclusive , with hand brush | t | 0.08 |  | 0
|  | Chapter 8.4. Fom 1 ... Fom 6 |  |  |  | 0
55 | TsC54B | Crushed stone foundation layer | m3 | 1.05 |  | 0
56 | CA03G | Reinforced concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class... В15 | m3 | 1.6 |  | 0
57 | CA03G | Reinforced concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class... В12,5 | m3 | 0.35 |  | 0
58 | CA03F | Plain concrete poured with classical means in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class.... B12,5 | m3 | 0.71 |  | 0
59 | CC01C | Concrete steel fittings OB 37 prepared in site workshop, with bar diameter up to 8 mm inclusive in isolated foundations | kg | 5.28 |  | 0
60 | CC01D | Concrete steel fittings OB 37 prepared in site workshop, with bar diameter more than 8 mm inclusive in isolated foundations | kg | 31.68 |  | 0
61 | CL57A | Mounting and fixing the embedded parts in monolith reinforced concrete: with weight less than 4 kg | kg | 70.58 |  | 0
62 | CB02A | Boxes from reusable panels, with boarding from short and super short wood planks to pour the concrete in forms, glass-shaped foundations and equipment platforms including support | m2 | 9.7 |  | 0
|  | Chapter 8.5. Chimney flue |  |  |  | 0
63 | CA02C | Plain concrete poured in equalizers, slopes, curves at height up to 35m inclusive , prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means B3,5 | m3 | 0.53 |  | 0
64 | CA03G | Reinforced concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class... В12,5 | m3 | 5.1 |  | 0
65 | CC01C | Concrete steel fittings OB 37 prepared in site workshop, with bar diameter up to 8 mm inclusive in isolated foundations | kg | 4.8 |  | 0
66 | CC01D | Concrete steel fittings OB 37 prepared in site workshop, with bar diameter more than 8 mm inclusive in isolated foundations | kg | 180.9 |  | 0
67 | CB02A | Boxes from reusable panels, with boarding from short and super short wood planks to pour the concrete in forms, glass-shaped foundations and equipment platforms including support | m2 | 13.8 |  | 0
68 | CG01A | Support layer for flooring executed from cement mortar M 150-T of 3 cm thickness with finely plastered surface (5 cm thick) | m2 | 1.96 |  | 0
69 | CG01A1 k=4 | Support layer for flooring executed from cement mortar M 150-T of 3 cm thickness with finely plastered surface.The difference for each 0,5 cm of support layer of mortar M 150-T, should be added or deducted | m2 | 1.96 |  | 0
70 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, all or partially embedded in concrete | tn | 1.33 |  | 0
71 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment. | t | 1.33 |  | 0
72 | IzD04A k=1.5 | Painting metallic articles and constructions with oil paint in 3 layers, executed from profiles with thickness between 8mm and 12mm inclusive, with hand brush | t | 1.33 |  | 0
|  | Chapter 8.6. Dry wall |  |  |  | 0
73 | TsC54B | Crushed stone foundation layer | m3 | 3.53 |  | 0
74 | CA02C | Plain concrete poured in equalizers, slopes, curves at height up to 35m inclusive , prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means B12,5 | m3 | 2.47 |  | 0
Total VAT 0 rate | [5 empty] | 0

## EEF
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solid biomass heating system in the gymnasium of Garbova village, Ocnita district
Site: | y
Section: |  | Electricity and lighting
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive ) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Assembling works |  |  |  | 0
1 |  | Install the following on existing support: |  |  |  | 0
2 | 08-01-061-1 | Security device (safety fuse SL11.11) | unit | 1 |  | 0
3 | 08-01-066-1 | lightning conductor, tension up to 10 kV (surge arrester LVA-440-В-К) | set | 1 |  | 0
4 | 08-03-573-4 | Suspended control cabinet (panel), height, width and depth, mm, up to (BZUM-TF-100-12) | unit | 1 |  | 0
5 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 2 |  | 0
6 | 08-03-600-1 | Meters mounted on ready support, monophase (ZCG112AS) | unit | 1 |  | 0
7 | 08-03-573-4 | Suspended control cabinet (panel), height, width and depth, 24 module box КmПн 2/24 IP55 | unit | 1 |  | 0
8 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 17 |  | 0
9 |  | Connecting rail YNS20-3-063 | unit | 2 |  | 0
10 |  | Rail РЕ and N YNN10-14-100 | unit | 4 |  | 0
11 | 08-03-573-4 | Suspended control cabinet (panel), height, width and depth, (extensive box К654У2) | unit | 1 |  | 0
12 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 1 |  | 0
13 |  | Plug socket with grounding contact IP54 | unit | 1 |  | 0
14 |  | Flexible cable КГ (А) LS 3х10 mm2 | m | 10 |  | 0
15 | 08-03-530-4 | General magnetic starter, separated, mounted on wall or column, power up to 40 A ПmА-0247 | unit | 9 |  | 0
16 | 08-03-603-1 | Box with descending transformers ЯТП-0,25-220/12 | unit | 1 |  | 0
17 | 08-03-594-2 | Source of light with luminescent light bulbs mounted separately on pivots, number of light bulbs, in source of light, 2 ALS.OPL 218 IP54 | 100 unit | 0.04 |  | 0
18 | 08-03-594-2 | Source of light with luminescent light bulbs mounted separately on pivots, number of light bulbs, in source of light, 2 СД 218 | 100 unit | 0.01 |  | 0
19 |  | Illuminating devices with fluorescent lights, ceiling ALS.OPL 218 IP54 | unit | 4 |  | 0
20 |  | Illuminating devices with compact fluorescent lights, ceiling CD 218 IP54 | unit | 1 |  | 0
21 |  | Torch СГВ-2 | unit | 1 |  | 0
22 |  | luminescent light bulbs ЛЛ-18 | unit | 8 |  | 0
23 |  | Compact luminescent light bulbs ЛЛК-18 | unit | 2 |  | 0
24 | 08-03-591-2 | One button switch, open type, hidden Iн=10А, Uн=220В IP43 | 100 unit | 0.02 |  | 0
25 | 08-03-591-8 | Plug socket open type, open switch socket | 100 unit | 0.01 |  | 0
26 | 08-02-472-3 | Earth binding conductor hidden in equalizer layer of floor, flat steel, section 100 mm2 (flat steel) | 100 m | 0.2 |  | 0
27 | 08-02-471-4 | Earth plug, vertical, round steel, diameter 16 mm (round steel) | 10 unit | 0.09 |  | 0
28 | 08-02-472-1 | Earth binding conductor: earth socket, horizontal, round steel, diameter 12 mm | 100 m | 0.8 |  | 0
29 | 08-02-146-1 | Cable up to 35 kV, fixed with applied clips, mass 1 m up to: 0,5 kg (ВВГнг(А)-LS sec, 3х1,5 mm2) | 100 m | 1.67 |  | 0
30 | 08-02-148-1 | Cable up to 35 kV in posed pipes, blocks and boxes, mass 1 m up to: 1 kg (ВВГнг(А)-LS sec, 3х1,5 mm2) | 100 m | 0.2 |  | 0
31 | 08-02-146-1 | Cable up to 35 kV, fixed with applied clips, mass 1 m up to: 0,5 kg (ВВГнг(А)-LS sec, 3х4 mm2) | 100 m | 0.03 |  | 0
32 | 08-02-146-1 | Cable up to 35 kV, fixed with applied clips, mass 1 m up to: 0,5 kg (ВВГнг(А)-LS sec, 3х10 mm2) | 100 m | 0.11 |  | 0
33 | 08-02-148-1 | Cable up to 35 kV in posed pipes, blocks and boxes, mass 1 m up to: 1 kg (ВВГнг(А)-LS sec, 3х10 mm2) | 100 m | 0.04 |  | 0
34 | 08-02-148-1 | Cable up to 35 kV in posed pipes, blocks and boxes, mass 1 m up to: 1 kg (ВВГнг(А)-LS sec, 3х16 mm2) | 100 m | 0.03 |  | 0
35 | 08-02-149-1 | Cable up to 35 kV suspended on steel cable, mass 1 m up to: 1 kg (ВВГнг(A)-LS sec, 3х16 mm2) | 100 m | 0.12 |  | 0
36 | 08-02-146-1 | Cable up to 35 kV, fixed with applied clips, mass 1 m up to: 0,5 kg (ВВГнг(А)-LS sec, 3х16 mm2) | 100 m | 0.14 |  | 0
37 | 08-02-146-1 | Cable up to 35 kV, fixed with applied clips, mass 1 m up to: 0,5 kg (ВВГнг-FRLS sec, 3x1,5 mm2) | 100 m | 0.07 |  | 0
38 | 08-02-141-1 | Cable up to 35 kV in trenches executed without cover, mass 1 m, up to: 1 kg (АПвзБбШп sec, 3х6 mm2) | 100 m | 0.25 |  | 0
39 | 08-02-148-1 | Cable up to 35 kV in posed pipes, blocks and boxes, mass 1 m up to: 1 kg (АПвзБбШп sec, 3х6 mm2) | 100 m | 0.06 |  | 0
40 | 08-02-146-1 | Cable up to 35 kV, fixed with applied clips, mass 1 m up to: 0,5 kg (АПвзБбШп sec, 3х6 mm2) | 100 m | 0.12 |  | 0
41 | 08-02-142-1 | Execute the bedding for one cable in trench (sand) | 100 m | 0.25 |  | 0
42 | 08-02-143-1 | Cover the cable posed in trench with brick for one cable | 100 m | 0.25 |  | 0
42A |  | Cable with copper wires ВВГнг(A)-LS sec, 3х1,5 mm2 | m | 187 |  | 0
43 |  | Cable with copper wires ВВГнг(A)-LS sec, 3х4 mm2 | m | 3 |  | 0
44 |  | Cable with copper wires ВВГнг(A)-LS sect. 3х10 mm2 | m | 15 |  | 0
45 |  | Cable with copper wires ВВГнг(A)-LS sect. 3х16 mm2 | m | 27 |  | 0
46 |  | Cable with copper wires ВВГнг(A)-FRLS sect. 3х1,5 mm2 | m | 7 |  | 0
|  | Cable with aluminium conductor armored АПвзБбШп sect. 3х6,0 mm2 | m | 43 |  | 0
47 | 08-02-407-6 | Steel pipe on constructions installed in primed channels executed, on flooring support, diameter up to 20 mm (steel pipe 20 mm) | 100 m | 0.13 |  | 0
48 | 08-02-411-1 | Metallic hosepipe, outer diameter up to 48 mm (metallic sleeve РЗ-ЦХ-Д20 mm) | 100 m | 0.09 |  | 0
49 | 08-02-411-2 | Metallic hosepipe, outer diameter up to 60 mm (metallic sleeve РЗ-ЦХ-Д50 mm) | 100 m | 0.04 |  | 0
50 | 10-06-034-14 | Different works: cable protection with plastic gutters, on brick or wood walls box size 40х20 | m | 15 |  | 0
|  | Chapter 2. Sanitary works |  |  |  | 0
51 | 34-02-003-1 | Execute polyethylene pipelines: up to 2 holes ПЭ д110mm | 1 km | 0.005 |  | 0
52 | 34-02-064-1 | Install supporting pillars for telephone network: one pair (mast H=3,0m Dn40 mm) | unit | 3 |  | 0
54 | 1 | Sand | m3 | 1.5 |  | 0
55 | 37 | Red bricks | unit | 100 |  | 0
56 | TsA02B | Manual digging of soil in limited spaces, under 1,00 m or over 1,00 m in width, executed without support, with vertical slope, in foundations, channels, drainages, twinning steps, in non-cohesive soil or lightly cohesive soil depth < 0,75 m middle ground | m3 | 4.5 |  | 0
57 | TsD01B | Scattering with shovel of loose soil, in uniform layers, of 10-30 cm thickness, with a throw of up to 3 m from piles, including smashing the clods, soil from middle ground | m3 | 3 |  | 0
58 | TsD05B | Mechanical compacting with rammer of 150-200 kg of piles in successive layers of 20-30 cm thickness, excluding watering each layer in part, filling made of cohesive soil | 100 m3 | 0.03 |  | 0
|  | Chapter 3. Equipment |  |  |  | 0
59 |  | Discharging rod LVA-440-В-К | unit | 1 |  | 0
60 |  | Control panel "BZUM-TF-100-12" | unit | 1 |  | 0
61 |  | Switch ВН 32-1Р/40 | unit | 1 |  | 0
62 |  | Automatic switch ВА47-29/1/С32 | unit | 1 |  | 0
63 |  | Active electric energy meter ZCG 112 AS, Iн=5-40А, U=220В | unit | 1 |  | 0
64 |  | 24 module box КmПн 2/24 IP55 | unit | 1 |  | 0
65 |  | Comutator ПП-1P-32 | unit | 1 |  | 0
66 |  | Automatic switch with one pole ВА47-29/1/С10 | unit | 2 |  | 0
67 |  | Automatic switch with one pole ВА47-29/1/C6 | unit | 3 |  | 0
68 |  | Automatic switch with one pole ВА47-29/1/C4 | unit | 5 |  | 0
69 |  | Automatic switch with one pole ВА47-29/1/B4 | unit | 1 |  | 0
70 |  | Automatic switch with one pole ВА47-29/1/C2 | unit | 3 |  | 0
71 |  | Automatic switch with one pole ВА47-29/1/B2 | unit | 2 |  | 0
72 |  | Plug-in connector box К654У2 | unit | 1 |  | 0
73 |  | Power switch ВН-32-1Р-32А | unit | 1 |  | 0
74 |  | Contactor - ПmА-0247 Uн=220В | unit | 9 |  | 0
75 |  | Mobile electric energy generator with diesel engine 220V/50Hz, 7,0 кVA, equipped with automatic connection to power grid | set | 1 |  | 0
Total VAT 0 rate | [5 empty] | 0

## ATM
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solid biomass heating system in the gymnasium of Garbova village, Ocnita district
Site: | y
Section: |  | Automated control and regulation system
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive ) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | 11-02-002-01 | Device installed on flange mix, mass, kg, up to: 1,5 ТТУ, ТТП, ТПГ100эк | unit | 11 |  | 0
2 | 11-01-001-01 | Constructions for device installations, mass, kg, up to: 1 (frame) | unit | 9 |  | 0
3 | 11-02-001-01 | Device installed on threaded mix, mass, kg, up to: 1,5, (mП4, mВП, Дm2010) | unit | 32 |  | 0
4 | 11-02-001-01 | Device installed on threaded mix, mass, kg, up to: 1,5, (draft gauge ТНmП-52-m2) | unit | 1 |  | 0
5 | 10-08-003-01 | Warning alarm CC-1 | unit | 1 |  | 0
6 | 11-02-001-01 | Device installed on threaded mix, mass, kg, up to: 1,5 (oxide detector RGD COO MP1) | unit | 1 |  | 0
7 | 11-03-001-01 | Devices installed on metalic constructions, pannels and consoles: device, mass, kg, up to 5 (detection device РОС-301) | unit | 1 |  | 0
8 | 11-02-001-01 | Device installed on threaded mix, mass, kg, up to: 1,5 (electronic regulator Danfoss) | unit | 1 |  | 0
9 | 11-02-002-01 | Device installed on flange mix, mass, kg, up to: 1,5 detection device ESM-10 | unit | 1 |  | 0
10 | 11-02-002-01 | Device installed on flange mix, mass, kg, up to: 1,5 detection device EMSU-10 | unit | 1 |  | 0
11 | 11-01-001-01 | Constructions for device installations, mass, kg, up to: 1 (tap) | unit | 29 |  | 0
12 | 11-06-002-04 | Electrical grid through tubes in panels and consoles: steel tubes D=15mm | 100 m | 0.12 |  | 0
13 | 08-02-407-6 | Steel pipe on constructions installed in primed channels executed, on flooring support, diameter up to 20 mm | 100 m | 0.16 |  | 0
14 | 11-08-002-01 | Connection of electrical grid through pipes to devices: water-gas pipelines, diameter of conventional section, up to 15 mm | 10 unit | 1.2 |  | 0
15 | 08-02-411-1 | Metallic hosepipe, outer diameter up to 15 mm (РЗ-ЦХ-Ш15) | 100 m | 0.13 |  | 0
16 | 10-06-034-14 | Various works: cable protection with plastic covers on wood or brick walls | m | 40 |  | 0
17 | 08-02-148-1 | Cable up to 35 kV in posed pipes, blocks and boxes, mass 1 m up to: 1 kg | 100 m | 2.18 |  | 0
18 | 08-02-412-9 | Introduce conductors in posed metallic pipes and hoses: each following mono- or multi-wire conductor in general mesh, summary section up to 6 mm2 ПВ1-0,38 sec,1x1,5 mm2 | 100 m | 0.1 |  | 0
19 |  | Signalling and control panel ЩУС - box type ЯУЭ-1263 dim. 1200x600x350 |  |  |  | 0
20 | 11-06-001-02 | Panel, mass, kg, up to: 100 size 1200х600х350 ЯУЭ1263 | unit | 1 |  | 0
21 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 60 |  | 0
22 | 11-08-001-04 | Connection of electrical grids to devices by glue | 100 units | 1.22 |  | 0
23 |  | Costs of materials |  |  |  | 0
24 |  | Selection device Г-16-225, В-16-225 | unit | 11 |  | 0
25 |  | Selection device Г16-80, В-16-80, 955-2 | unit | 18 |  | 0
26 |  | Steel pipe D=15mm | m | 12 |  | 0
27 |  | Steel pipe D=20mm | m | 16 |  | 0
28 |  | Metallic hosepipe D=15mm | m | 14 |  | 0
29 |  | Cable trench | m | 40 |  | 0
30 |  | Cable КВВГнг-LS sect. 4х1,5mm2 | m | 120 |  | 0
31 |  | CableКВВГнг-LS sect. 5х1,5mm2 | m | 80 |  | 0
32 |  | Cable КВВГнг-LS sect. 7х1,5mm2 | m | 18 |  | 0
33 |  | Conductor ПВ1-0,38 sec, 1x1,5mm2 | m | 10 |  | 0
|  | Chapter 2. Equipment |  |  |  | 0
34 |  | Thermometer ТТУ, ТТП | unit | 9 |  | 0
35 |  | ThermometerТПГ100эк-m1 | unit | 2 |  | 0
36 |  | Sensor relay level РОС-301 | unit | 1 |  | 0
37 |  | Manometer mП4-У, mВП-Ух0,6 | unit | 26 |  | 0
38 |  | ManometerДm2010С | unit | 6 |  | 0
39 |  | Device to measure ТНmП-52-m1 | unit | 1 |  | 0
40 |  | Acoustic alarm СС-1 | unit | 1 |  | 0
41 |  | Detector CO RGD COOMP1 | unit | 1 |  | 0
42 |  | Electronic themperature regulator Danfoss | unit | 1 |  | 0
43 |  | Signalling and control panel ЩУС-ЯУЭ-1263 1200x600x350mm IP54 | unit | 1 |  | 0
44 |  | Automatic switch ВА47-29/1/С2 | unit | 6 |  | 0
45 |  | Contactor УП5311 | unit | 7 |  | 0
46 |  | Relay ПЭ37 | unit | 20 |  | 0
47 |  | Relay РСВ19-11 | unit | 3 |  | 0
48 |  | Relay РСВ19-31 | unit | 2 |  | 0
49 |  | Button ABLFS-22 | unit | 4 |  | 0
50 |  | Signalling device АD-22DS | unit | 9 |  | 0
51 |  | Diode Д246 | unit | 9 |  | 0
52 |  | Terminal block Бз24-4П | unit | 6 |  | 0
Total VAT 0 rate | [5 empty] | 0

## BK
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solid biomass heating system in the gymnasium of Garbova village, Ocnita district
Site: | y
Section: |  | Water and sewage
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive ) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | External water supply pipelines |  |  |  | 0
|  | Chapter 1. Mounting pipelines |  |  |  | 0
1 | TsC03B1 | Mechanical digging with excavator of 0,40-0,70 mc, with internal combustion engine and hydraulic control, in ground with natural humidity, unloading in piles ground category II | 100 m3 | 0.25 |  | 0
2 | TsA20B | Manual digging of soil, in slopes, holes dug with excavator or scraper, to fill in the digging of slope profile, in middle ground | m3 | 0.8 |  | 0
3 | TsD02A1 | Scattering loose soil from ground category I or II, executed by bulldozer on tracks 65-80 CP, in layers of 15-20 cm thickness | 100 m3 | 0.17 |  | 0
4 | TsD05A | Mechanical compacting with rammer of 150-200 kg of piles in successive layers of 20-30 cm thickness, excluding watering each layer in part, filling made of non-cohesive soil | 100 m3 | 0.17 |  | 0
5 | TsD01B | Scattering with shovel of loose soil, in uniform layers, of 10-30 cm thickness, with a throw of up to 3 m from piles, including smashing the clods, soil from middle ground | m3 | 4.3 |  | 0
6 | TsD04B | Manual punning of piles made in horizontal or inclined digging at 1/4, including watering each soil layer in part with 10 cm thickness of cohesive soil | m3 | 4.3 |  | 0
7 | AcF03A | Filling the trenches for water and sewage pipelines, as sub-layer, protection layer, isolation layer or flange layer for drainage tubes, executed with sand | m3 | 1.1 |  | 0
8 | AcE10A | Executing the manholes from ready-made reinforced concrete elements, for water supply circular (ring) with diameter 1,0 m, in soil without underground water | m3 | 0.77 |  | 0
9 | AcE10A1 | Ready-made reinforced concrete elements of manholes, in soil without underground water. Note: resource with 0,00 (zero) norm is in accordance with the project | unit | 1 |  | 0
10 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment. | t | 0.02 |  | 0
11 | IzD04A | Painting the articles and metallic constructions with oil paint in 2 layers, executed from profiles, between 8mm-12mm thickness inclusive , with hand brush | t | 0.02 |  | 0
12 | TsC54B | Crushed stone foundation layer | m3 | 0.31 |  | 0
13 | DB16A | Asphalt concrete coat with small aggregates, executed at cold temperatures, in thickness of 2,5 cm manually laid | m2 | 3.08 |  | 0
14 | AcA52A | Polyethylene pipe, for water pipes embedded in trench, with diameter 20 mm. Note: type of polyethylene pipe and warning band will be included according to the project PE80 SDR17,6 PN6 | m | 35 |  | 0
15 | AcF11C | Washing PVC, cast, cement, polyethylene pipes etc 20-75 mm, for drinking water after mounting and combining, before reception | m | 35 |  | 0
16 | AcF12A | Tightness test of polyethylene pipes mounted in trenches for water and sewage pipelines, with diameter up to 100 mm | m | 35 |  | 0
17 | AcB01A | Mounting fittings with manual or mechanical functioning (tubs, taps, vents), in water and sewage pipes, with diameter 15 mm (flange lock valve 15h9р) | unit | 1 |  | 0
18 | AcA26A | Connect with flanges the joining parts, flanges, including blind flanges and fittings with diameter 15 mm (free flange) | unit | 2 |  | 0
19 | IC44B | Manufacture, mounting and cementing the pipes through walls, pipe with diameter 89х3,7 mm (sleeve L=0,30 m) | unit | 2 |  | 0
|  | Chapter 2. Assembling works |  |  |  | 0
20 | 07-04-030-01 | Fountain pump, submersible electric motor, | set | 1 |  | 0
|  | Chapter 3. Equipment |  |  |  | 0
21 |  | Pump "EVJ 1,8-50-0,5": Q=0,5 m3/h; Н=40,0 m; N=0,75 кВт; "HIDROPOMPA" or similar | set | 1 |  | 0
|  | External sewage pipelines |  |  |  | 0
22 | TsC03B1 | Mechanical digging with excavator of 0,40-0,70 mc, with internal combustion engine and hydraulic control, in ground with natural humidity, unloading in piles ground category II | 100 m3 | 0.19 |  | 0
23 | TsA20B | Manual digging of soil, in slopes, holes dug with excavator or scraper, to fill in the digging of slope profile, in middle ground | m3 | 0.6 |  | 0
24 | TsD02A1 | Scattering loose soil from ground category I or II, executed by bulldozer on tracks 65-80 CP, in layers of 15-20 cm thickness | 100 m3 | 0.12 |  | 0
25 | TsD05A | Mechanical compacting with rammer of 150-200 kg of piles in successive layers of 20-30 cm thickness, excluding watering each layer in part, filling made of non-cohesive soil | 100 m3 | 0.12 |  | 0
26 | TsD01B | Scattering with shovel of loose soil, in uniform layers, of 10-30 cm thickness, with a throw of up to 3 m from piles, including smashing the clods, soil from middle ground | m3 | 3.1 |  | 0
27 | TsD04B | Manual punning of piles made in horizontal or inclined digging at 1/4, including watering each soil layer in part with 10 cm thickness of cohesive soil | m3 | 3.1 |  | 0
28 | AcF03A | Filling the trenches for water and sewage pipelines, as sub-layer, protection layer, isolation layer or flange layer for drainage tubes, executed with sand | m3 | 0.27 |  | 0
29 | AcE15A | Execution of manholes from ready-made reinforced concrete, for sewage, circular (rings) with diameter 2,0 m, in soil without underground water | m3 | 2.3 |  | 0
30 | AcE15A1 | Ready-made reinforced concrete elements, of manholes, circular (rings) with diameter 2,0 m, for sewage, in soil without underground water. | unit | 1 |  | 0
31 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment. | t | 0.02 |  | 0
32 | IzD04A | Painting the articles and metallic constructions with oil paint in 2 layers, executed from profiles, between 8mm-12mm thickness inclusive , with hand brush | t | 0.02 |  | 0
33 | CD50A | Plain brick masonry, format 250 x 120 x 65 in outer walls with height up to 4 m | m3 | 0.05 |  | 0
34 | TsC54B | Crushed stone foundation layer | m3 | 0.31 |  | 0
35 | DB16A | Asphalt concrete coat with small aggregates, executed at warm temperatures, in thickness of 2,5 cm manually laid | m2 | 3.08 |  | 0
36 | AcA07B | Mounting in the ground, outside buildings, PVC pipes type 4(G) or 3(M), with diameter 110 mm SN4 SDR41 | m | 5 |  | 0
|  | Water pipeline |  |  |  | 0
|  | Chapter 1. Sanitary works |  |  |  | 0
37 | SF51A | Water level measuring without meter, having the diameter of the branch 15 mm | set | 1 |  | 0
38 | SD19A | Straight-way valve with threaded sockets, with diameter 15 mm (stopping valve 15Б1бк) | unit | 1 |  | 0
39 | SD18A | Garden hosepipe, mounted in soil with diameter 15 mm | set | 1 |  | 0
40 | SA01A | Galvanized steel pipe for installations, mounted in industrial constructions, with diameter 15 mm | m | 6 |  | 0
41 | SF01A | Tightness test under pressure of hot or cold pipeline executed on steel, galvanized pipelines, for installations, longitudinally welded, with diameter 3/8"-2" | m | 6 |  | 0
42 | SF05A | Washing hot or cold water pipelines, executed from steel, galvanized pipes, with diameter 3/8"-2" | m | 6 |  | 0
43 | IzJ09B | Painting the tin cover of pipes and devices with 2 layer oil paint, including priming | m2 | 0.36 |  | 0
44 | SD19A | Straight-way valve with threaded sockets, with diameter 15 mm (water valve) | unit | 1 |  | 0
45 | AcA52A | Polyethylene pipe, for water pipes embedded in trench, with diameter 20 mm. Note: type of polyethylene pipe and warning band will be included according to the project PE80 SDR21 PN6 | m | 3 |  | 0
46 | TsA03E | Manual digging of soil in limited spaces, under 1,00 m width, executed without supports, at inclined slope in foundations, trenches, etc., ground with average cohesion or very cohesive, up to 1,5 m depth middle ground | m3 | 1.4 |  | 0
47 | TsD01B | Scattering with shovel of loose soil, in uniform layers, of 10-30 cm thickness, with a throw of up to 3 m from piles, including smashing the clods, soil from middle ground | m3 | 1.4 |  | 0
48 | TsD04B | Manual punning of piles made in horizontal or inclined digging at 1/4, including watering each soil layer in part with 10 cm thickness of cohesive soil | m3 | 1.4 |  | 0
49 | CA03F | Plain concrete poured with classical means in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class.... В7.5 | m3 | 0.06 |  | 0
50 | IA32A | Expending vessel closed with membrane, with capacity up to 50 l (membrane tank Zilmet Ultra-Pro) | unit | 1 |  | 0
|  | Chapter 2. Equipment |  |  |  | 0
51 |  | Cold water meter Dn15 mm | unit | 1 |  | 0
|  | Sewage pipeline |  |  |  | 0
52 | SB08E | Pipe from plastic material for sewage, connected with rubber set, mounted apparently or under the flooring, with diameter 100 mm polypropylene | m | 13 |  | 0
53 | SB08C | Pipe from plastic material for sewage, connected with rubber set, mounted apparently or under the flooring, with diameter 50 mm polypropylene | m | 10 |  | 0
54 | SF04A | Tightening and functioning test of sewage system made of cast tubes, for drainage, vynil polychrome pipe, non-plasticised, light or from plastic material, ductile iron pipe with diameter up to 100 mm inclusive | 10 m | 2.3 |  | 0
55 | SB08E | Pipe from plastic material for sewage, connected with rubber set, mounted apparently or under the flooring, with diameter 100 mm (polypropylene fittings 15%) | m | 2 |  | 0
56 | SB08C | Pipe from plastic material for sewage, connected with rubber set, mounted apparently or under the flooring, with diameter 50 mm (polypropylene fittings 15%) | m | 1.5 |  | 0
57 | SB10E | Connecting part (plain ramification) from plastic material for sewage, combined with rubber, with diameter 100 mm (polyethylene review) | unit | 1 |  | 0
58 | SB10E | Connecting part (plain ramification) from plastic material for sewage, combined with rubber, with diameter 100 mm (polyethylene cleaning) | unit | 2 |  | 0
59 | SB10C | Connecting part (plain ramification) from plastic material for sewage, combined with rubber, with diameter 50 mm (polyethylene cleaning) | unit | 1 |  | 0
60 | SB24E | Enamel iron floor trap, simple, with diameter 100 mm (steel trap) | unit | 1 |  | 0
61 | AcA25A | Mounting through electric welding of connecting parts, of steel, in position, with diameter 100x50 mm (steel cone) | unit | 6 |  | 0
62 | SB10C | Connecting part (plain ramification) from plastic material for sewage, combined with rubber, with diameter 50 mm (trap cleaning) | unit | 6 |  | 0
63 | CA03F | Plain concrete poured with classical means in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according art. CA01, poured with classical means, plain concrete class.... В7.5 | m3 | 0.24 |  | 0
64 | SC06A | Dripping cleanser (with one section) for dishes, having a plastic drainage pipe, mounted on consoles fixed on brick walls | unit | 1 |  | 0
Total VAT 0 rate | [5 empty] | 0

## SIP
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solid biomass heating system in the gymnasium of Garbova village, Ocnita district
Site: | y
Section: |  | Anti fire system
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive ) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Assembling works |  |  |  | 0
1 | 10-08-002-03 | Automatic alarm PC: thermal, smoke, light, protection against explosion ИП-105-2/1 | unit | 4 |  | 0
2 | 10-08-002-05 | Automatic OC alarm: crash, without electromagnetic or piezoelectric contact, installed on glass ИПР-2-01 | unit | 1 |  | 0
3 | 10-08-001-06 | Receiving devices: Devices "ПС" for reception and control, warning. Concentrator: 4 ways main block (Varta 1/2 GSM) | unit | 1 |  | 0
4 | 10-08-019-01 | Various electric clock equipment: Wall mounted ramification box | unit | 1 |  | 0
5 | 10-08-003-01 | Warning device with the capacity SA-913F | unit | 1 |  | 0
6 | 08-02-148-1 | Cable up to 35 kV in posed pipes, blocks and boxes, mass 1 m up to: 1 kg КПСЭСнг(А)-FRLS 2x2x0,2 | 100 m | 0.3 |  | 0
7 | 08-02-148-1 | Cable up to 35 kV in posed pipes, blocks and boxes, mass 1 m up to: 1 kg ВВГнг-FRLS sec, 2х1,5mm2 | 100 m | 0.06 |  | 0
8 | 08-01-121-1 | Stationary acid accumulator, type: С-1, СК-1 1270 ВАТТ | unit | 1 |  | 0
9 | 10-08-019-01 | Various electric clock equipment: Wall mounted ramification box УК-2П | unit | 2 |  | 0
10 | 10-06-034-14 | Various works: cable protection with plastic gutters, on wood or brick walls ТmК-1020 | m | 36 |  | 0
|  | Chapter 2. Equipment |  |  |  | 0
11 |  | Heat and fire detectors (10% reserve) ИП-105-2/1 | unit | 4 |  | 0
12 |  | Fire detectors ИПР-2-01 | unit | 1 |  | 0
13 |  | Fire signal reception device Varta 1/2 GSM | unit | 1 |  | 0
14 |  | Metallic box | unit | 1 |  | 0
15 |  | Alarm system with flashing lights, 12V, SA-913F | unit | 1 |  | 0
16 |  | Accumulator 12V7Ah | unit | 1 |  | 0
17 |  | Motor pump to put down fires with refilling debit 36 m3/hour and vacuum depth 6 m, with hose pipe d=50mm and length 60m, mН-13/60 or similar | unit | 1 |  | 0
18 |  | Fire extinguisher OP-5 | unit | 2 |  | 0
Total VAT 0 rate | [5 empty] | 0

## FSS
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solid biomass heating system in the gymnasium of Garbova village, Ocnita district
Site: | y
Section: |  | Fuel system
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive ) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
0
0
Total VAT 0 rate | [5 empty] | 0

## Commiss
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solid biomass heating system in the gymnasium of Garbova village, Ocnita district
Site: | y
Commissioning
No. | Item | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
1 |  | Training of operators | course | 1 |  | 0
2 |  | Measure the emissions | test | 1 |  | 0
3 |  | Measure performance indicators | test | 1 |  | 0
4 |  | Commissioning integral system | system | 1 |  | 0
Total excluding VAT : | [5 empty] | 0
The bidder is responsible for any item that was not attributed a unit price and will be provided without additional costs for the UNDP

## Maintenance
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solid biomass heating system in the gymnasium of Garbova village, Ocnita district
Site: | y
Service and Maintenance works for 3-years of operation
No. | Item | Description of item | Periodicity | Quantity for 3 years | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
1 |  | Maintenance works and commissioning of heating system at the beginning of heating season | annual | 3 |  | 0
2 |  | Periodic maintenance works at the end of heating season | annual | 3 |  | 0
3 |  | Intervention and reparation of equipment in case of emergency | case | 3 |  | 0
4 |  | Telephonic assistance in using the system | permanent | 1 |  | 0
Total excluding VAT : | [5 empty] | 0
* Any equipment or component that requires replacement within the 3 years period and was not included in the list of wear parts shall be treated as a warranty case and must be provided by the contractor at no additional cost

## Boiler
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solid biomass heating system in the gymnasium of Garbova village, Ocnita district
Site: | y
Minimum specifications of boiler
No | Item | Requirements | Suggested requirements | Quantity | Unit price USD | Total, USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | Boiler | Boiler model: |  | 2 | 1 | 2
Fuel type: agro-pellets, type E, EN 14961-6 (according to Technical Specifications description) *
Limits of emission: EN 303-5:2012 Class 3
Q1 = 100 kW, Q2 = 150kW **
Productivity: minimum 80% ****
Work pressure: ≥1.5 bar
Maximum admitted temperature at operation: ≥85 °C
Power tension: 230V/50Hz
Warranty for active components: 3 years
Warranty for passive components: 5 years
Burner cleaning: automatic cleaning system of burner through mechanical means
Diameter of smoke chimney mm 369mm***:
Capacity of fuel tank VQ1 = 510 L, VQ2=890 L:
Boiler assembling scheme in existing boiler room in accordance with the normative in force *****
Total excluding VAT : | [5 empty] | 2
* Specify type of fuel in accordance with the producer's recommendation
** Based on E type biofuel in accordance with the Technical Specifications Description.
*** The bidder may suggest a boiler with higher or lower diameter than specified in project documentation, provided that the smoke chimney is compatible with the boiler and ensures its optimal operation, and the costs are adjusted accordingly in financial offer.
**** Specify only numerical value. Do not include text
***** The bidder will include an illustration to show the location of boilers in the boiler room by indicating main dimensions