## SITE
REF: | ITB
Lot: | x | Installation of biomass heating system and solar hot water production system in the kindergarten of Copceac village, Stefan Voda district
Site: | y
Consolidated price list |  |  |  | Estimated amount in USD, 0 rate VAT
Cost Composition / Section
1 | Territory development |  |  | 0
2 | Thermomechanics |  |  | 0
3 | Solar hot water system |  |  | 0
4 | Heating and ventilation |  |  | 0
5 | General construction works |  |  | 0
6 | Electricity and lighting |  |  | 0
7 | Automated control and regulation system |  |  | 0
8 | Water supply and sewage |  |  | 0
9 | Fire safety system |  |  | 0
10 | Fuel supply system |  |  | 0
11 | Commissioning |  |  | 0
12 | Service and Maintenance works for 3-years of operation |  |  | 0
| Total price of works |  |  | 0
No | Parameter |  | Unit | Value
1 | Annual heat consumption |  | MWh | 265.34
2 | Boiler efficiency at nominal output |  | % | 0%
3 | Fuel demand |  | MWh
4 | Net calorific value of the test fuel |  | MJ/ton | 15000
5 | Net calorific value of the test fuel |  | MWh/ton | 4.1667
6 | Annual fuel consumption |  | tone
7 | Estimated fuel price |  | USD/ton | 110
8 | Annual fuel cost |  | USD
9 | Discount rate |  | % | 10%
10 | Expected lifetime of the boiler |  | years | 10
11 | Current value (VC) of fuel |  | USD
Total life-cycle cost (PW + VC fuel cost) |  |  | USD
Bidder: |  |  | Signature
No changes to the initial structure of this document are allowed. Any modifications made in the document, may result in Bidder's disqualification.

## TA
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Installation of biomass heating system and solar hot water production system in the kindergarten of Copceac village, Stefan Voda district
Site: | y
Section: |  | Territory development
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Platform for containers |  |  |  | 0
1 | DA06B2 | Layer of cylindrical natural aggregates having the function of filtering, ventilation, anti-freezing and anti-cracking proof, mechanically laid, with sand | m3 | 0.7 |  | 0
2 | DA06B1 | Layer of cylindrical natural aggregates having the function of filtering, ventilation, anti-freezing and anti-cracking proof, mechanically laid, with ballast | m3 | 0.7 |  | 0
3 | CG22A | Plain concrete flooring, Class C 10/8 (Bc 10/B 150), 10 cm-thick, plastered, levelled, poured on-site, b=10 cm | m2 | 6 |  | 0
4 | DE11A | Precast small kerbs with section 10x15 cm to delimitate sidewalks placed on concrete base B-15, БР 100.20.8 | m | 24 |  | 0
| CO06A4 | Pens from wire fence with round steel frame panels fixed on precast concrete poles installed 2 m apart from interax coated with crushed stones | m | 20 |  | 0
| price | Steel poles to fix sheets including fasteners of D 40mm | unit | 10 |  | 0
| price | Steel sheets Eurogard 2,5x1,5m | unit | 8 |  | 0
|  | Equipment |  |  |  | 0
5 | Company price | Metal ash containers with lid, D = 600mm, H = 1000mm | unit | 6 |  | 0
6 | Company price | Wheelbarrow with steel bucket, Vbucket =0,1m3 | unit | 1 |  | 0
Total VAT (0 rate) | [5 empty] | 0

## TM
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Installation of biomass heating system and solar hot water production system in the kindergarten of Copceac village, Stefan Voda district
Site: | y
Section: |  | Thermomechanics
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. General construction works |  |  |  | 0
1 | IA20A | Screwed in safety valve with nominal D 1/2"...1" (Safety valve D25mm, P=1.0 MPA ) | unit | 2 |  | 0
2 | IA20A | Screwed in safety valve with nominal D = 1/2"...1" (Safety valve D20mm, P=1.0 MPA ) | unit | 2 |  | 0
3 | ID06A | Air relief valve with mobile key for central heating systems with nominal D = 1/4" (automated brass venting valve/vent pipe/D15mm ) | unit | 4 |  | 0
4 | ID05B | Lockable screw down valve with drawer, with flange for central heating systems, with nominal D= 50...65 mm (Flange Straight-way valve D50mm, P=1.0 MPa) | unit | 4 |  | 0
5 | ID04A | Straight-way or restraint valve with sockets for central heating system with nominal D= 1/2" -1" (Straight-way valve with sockets D20mm, P=1.0 MPa) | unit | 7 |  | 0
6 | ID04A | Straight-way or restraint valve with sockets for central heating system with nominal D 1/2" -1" (Straight-way valve with sockets D25mm, P=1.0 MPa) | unit | 11 |  | 0
7 | ID04C | Straight-way or restraint valve with sockets for central heating system with nominal D= 2" (Straight-way valve with sockets D50mm, P=1.0 MPa) | unit | 6 |  | 0
8 | ID04B | Straight-way or restraint valve with sockets for central heating system with nominal 1 1/4" -1 1/2" (Straight-way valve with sockets D32mm, P=1.0 MPa) | unit | 1 |  | 0
9 | VC24A | Elastic support of ventilator with rubber elastic support (elastic compensator for pump installation D50mm, P=1.0 MPa) | unit | 4 |  | 0
10 | VC24A | Elastic support of ventilator with rubber elastic support (elastic compensator for pump installation D25mm, P=1.0 MPa) | unit | 4 |  | 0
11 | VC24A | Elastic support of ventilator with rubber elastic support (elastic compensator for pump installation D20mm, P=1.0 MPa) | unit | 2 |  | 0
12 | ID04A | Straight-way or restraint valve with sockets for central heating system with nominal D 1/2" -1" (Non-return valve D25mm, P=1.0 MPa) | unit | 4 |  | 0
13 | ID04C | Straight-way or restraint valve with sockets for central heating system with nominal D= 2" (Non-return valve D50mm, P=1.0 MPa) | unit | 2 |  | 0
14 | ID04A | Straight-way or restraint valve with sockets for central heating system with nominal D= 1/2" -1" (Non-return valve D20mm, P=1.0 MPa) | unit | 1 |  | 0
|  | Chapter 1.2. Fine precast for boiler |  |  |  | 0
15 | ID03A | Three way plug valve, with flanges and stuffing, for central heating installations, nominal diameter 15 mm (three way Straight-way valve for manometer, D10mm, P=1.0 MPa) | unit | 4 |  | 0
16 | ID03A | Three way plug valve, with flanges and stuffing, for central heating installations, nominal diameter 15 mm (three way Straight-way valve for manometer D15mm, P=1.0 MPa) | unit | 4 |  | 0
|  | Chapter 1.3. Pipelines |  |  |  | 0
17 | IC35B | High-density polypropylene casted pipe installed to connect the heating bodies or devices in central heating systems with outer diameter 20x2,2 mm PE with frills | m | 2 |  | 0
18 | IC11F | Black longitudinally welded steel pipe for installations, mounted by welding in columns, in central heating systems for residential and social-cultural buildings, the pipe having the diameter of 45х2,5mm | m | 6 |  | 0
19 | IC12A | Black longitudinally welded steel pipe for constructions, mounted by welding in supply pipes in central heating systems for residential and social-cultural buildings, the pipe having the outer diameter and wall thickness 57х3mm | m | 16 |  | 0
20 | IC12C | Seamless or longitudinally welded steel pipe for structures, mounted through welding in distribution pipelines, in central heating systems for residential and social-cultural buildings, the pipe having the outer diameter and wall thickness of 76х3mm | m | 27 |  | 0
21 | IC11C | Black steel pipe welded longitudinally for structures, non-threaded, mounted through welding in columns, in central heating system for residential and social-cultural buildings, the pipe having the diameter of 20х2,8mm steel | m | 20 |  | 0
22 | IC11C | Black steel pipe welded longitudinally for structures, non-threaded, mounted through welding in columns, in central heating system for residential and social-cultural buildings, the pipe having the diameter of 25х2,8m | m | 12 |  | 0
23 | IC11E | Black steel pipe welded longitudinally for structures, non-threaded, mounted through welding in columns, in central heating system for residential and social-cultural buildings, the pipe having the diameter of 32х2,8m | m | 9 |  | 0
24 | IC11D | Black steel pipe welded longitudinally for structures, non-threaded, mounted through welding in columns, in central heating system for residential and social-cultural buildings, the pipe having the diameter of 32х2,8mm | m | 6 |  | 0
25 | IC11E | Black steel pipe welded longitudinally for structures, non-threaded, mounted through welding in columns, in central heating system for residential and social-cultural buildings, the pipe having the diameter of 40х2,8mm | m | 16 |  | 0
26 | IC11F | Black steel pipe welded longitudinally for structures, non-threaded, mounted through welding in columns, in central heating system for residential and social-cultural buildings, the pipe having the diameter of 50х3,2mm | m | 16 |  | 0
27 | IC11C | Black steel pipe welded longitudinally for structures, non-threaded, mounted through welding in columns, in central heating system for residential and social-cultural buildings, the pipe having the diameter of 20х2,8mm | m | 14 |  | 0
28 | IzA08A | Manually painted pipes with oil paint with outer diameter up to 34 mm including | m | 21 |  | 0
29 | IzA08B | Manually painted pipes with oil paint with outer diameter more than 34mm | m2 | 10.15 |  | 0
30 | IE03A | Leak-proof (tightness) test of feeding pipelines for heating devices (aerothermal, thermal convectors, plinth convectors, etc.) at pressure, the pipe having the diameter of 3/8" ... 1" | m | 46 |  | 0
31 | IE03B | Leak-proof (tightness) test of feeding pipelines for heating devices (aerothermal, thermal convectors, plinth convectors, etc.) at pressure, the pipe having the diameter of 1 1/4" ... 2" | m | 53 |  | 0
32 | IE03C | Leak-proof (tightness) test of feeding pipelines for heating devices (aerothermal, thermal convectors, plinth convectors, etc.) at pressure, the pipe having the diameter of 54 x 3,5 ... 83 x 3,5 mm | m | 43 |  | 0
33 | IE04A | Dilatation and contraction and functioning test of feeding pipelines for heating devices (aerothermal, thermal convectors, plinth convectors, etc.) at pressure, the pipe having the diameter of 3/8" ... 1" | m | 46 |  | 0
34 | IE04B | Dilatation and contraction and functioning test of feeding pipelines for heating devices (aerothermal, thermal convectors, plinth convectors, etc.), pipe having the diameter of 1 1/4" ... 2" | m | 53 |  | 0
35 | IE04C | Dilatation and contraction and functioning test of feeding pipelines for heating devices (aerothermal, thermal convectors, plinth convectors, etc.), pipe having the diameter of 54 x 3,5 ... 83 x 3,5 mm | m | 43 |  | 0
|  | Chapter 1.4. Smoke channels |  |  |  | 0
47 | CL20A | Manufactured ventilation grids from black sheets, with manual blinds painted and installed in masonry (ash evacuation flap D100mm, S=4.0mm, stainless steel) | unit | 2 |  | 0
48 | AcA25B | Electric welding installation of connecting parts from stainless steel sheet with the diameter 125-250 mm (Double smoke chimney in izolation S=50mm D180mm l=2,5m) | unit | 1 |  | 0
49 | AcA25B | Electric welding installation of connecting parts from stainless steel sheet with diameter 125-250 mm (Double smoke chimney in izolation S=50mm D180mm L=2.8m,) | unit | 1 |  | 0
50 | AcA25B | Electric welding installation of connecting parts from stainless steel sheet, in position, having the diameter 125-250 mm (Double smoke chimney in izolation S=50mm, D180mm, L=1.5m) | unit | 4 |  | 0
51 | AcA25B | Electric welding installation of connecting parts from stainless steel sheet having the diameter 125-250 mm (Double smoke chimney in izolation D180, S=50mm, a=90*C, L=0.45m, ) | unit | 1 |  | 0
52 | AcA25B | Electric welding installation of connecting parts from stainless steel sheet having the diameter 125-250 mm (Double smoke chimney in izolation S=50mm D=180mm, l= 1.4m) | unit | 1 |  | 0
53 | CL20A | Manufactured ventilation grids from black sheets, with manual blinds painted and installed in masonry (Siber D180mm S=3.5mm, L=22mm) | unit | 1 |  | 0
54 |  | junction 160x350mm on smoke chimney D180mm, S=3.5mm. H=0.12m | unit | 1 |  | 0
55 | CL20A | Manufactured ventilation grids from black sheets, with manual blinds painted and installed in masonry (Explosive valve/Safety flap/160x350mm, S=1.5mm) | unit | 1 |  | 0
56 | AcA25B | Electric welding installation of connecting parts from steel, in position, having the diameter 125-250 mm (Round lenticular compensator for smoke channels with one lenticular D180mm, S=3.5) | unit | 1 |  | 0
57 | AcA25B | Electric welding installation of connecting parts from steel, in position, having the diameter 125-250 mm (Flange D180- - -D280mm, S=4mm) | unit | 4 |  | 0
58 |  | junction 500x200mm - -D250mm, S=3.5mm, L=0.3m, | unit | 1 |  | 0
59 | AcA31C | Electric welding installation of flanges or connecting parts, from steel, at the end of pipes, having the diameter 300-400 mm (Flange D250- - -D360mm, S=2mm of thermo-insulation protection) | unit | 1 |  | 0
62 | CR03A | Wood panel made of the crushing of roundwood-shaving and wood-shaving rulers for rural constructions, executed in walls (Support under the tank 0.5 m3, wood 150x200x650mm, 2 unit) | м3 | 0.04 |  | 0
63 | IzA08B | Manually painted pipes with oil paint having the diameter more than 34 mm (cos) | m2 | 7 |  | 0
|  | Chapter 1.5. Insulation |  |  |  | 0
64 | IzJ13A | Sealing sheet panels connected with roving ROMTIX thermo-insulating tubes D 76, S=25mm, ARMOFLEX | m | 7 |  | 0
65 | IzJ13A | Sealing sheet panels connected with roving ROMTIX thermo-insulating tubes D 57, S=25mm, ARMOFLEX | m | 16 |  | 0
66 | IzJ13A | Sealing sheet panels connected with roving ROMTIX thermo-insulating tubes D 45, S=25mm, ARMOFLEX | m | 11 |  | 0
67 | IzJ13A | Sealing sheet panels connected with roving ROMTIX thermo-insulating tubes D 38, S=25mm, ARMOFLEX | m | 8 |  | 0
68 | IzJ13A | Sealing sheet panels connected with roving ROMTIX thermo-insulating tubes D 32, S=25mm, ARMOFLEX | m | 16 |  | 0
69 | IzJ13A | Sealing sheet panels connected with roving ROMTIX thermo-insulating tubes D 25, S=25mm, ARMOFLEX | m | 12 |  | 0
70 | IzH07A | Insulation of pipes with mineral wool or glass mats SPS 1 type, ready-made, sewed with zinc steel wire on wire mesh on one side, thickness 20; 30; 40, 50 or 60 mm, to the pipes with a circumference over thermo insulation below 35 cm, inclusive (Glass wool mats covered with metal mesh (two-sided mesh N12-1.2, brand 125)) 0.1912m3 b=40mm | m2 | 4.78 |  | 0
71 | IzI07A1 | Protection of pipe thermal insulation using 0,5 mm-thick black or zinc-coated sheets fixed with self-tapping screws with semi-round cleaved head, having the pipe circumference over the thermal insulation up to 0,35 m, assembling (Thin galvanized steel sheet S=0.5mm, GOST 14918-80* ) | m2 | 8.15 |  | 0
72 | IzI07A2 | Protection of pipe thermal insulation using 0,5 mm-thick black or zinc-coated sheets fixed with self-tapping screws with semi-round cleaved head, having the pipe circumference over the thermal insulation up to 0,35, assembling | m2 | 8.15 |  | 0
|  | Chapter 2. Assembling works |  |  |  | 0
73 | IA13A | Monobloc steel water heating boiler (hot water 90/70 degrees), with calorific power up to 70 kw | unit | 1 |  | 0
74 | IA38A | Circulation pump (recirculation) mounted on the existing pipe by flanges, having a diameter up to 2 "(50 mm) | unit | 5 |  | 0
75 | ID03C | Three way plug valve, with flanshes and stuffing, for central heating systems, nominal diameter 65 mm | unit | 1 |  | 0
76 | IA27A | Condensation reservoir, mounted on a base, with the capacity of 0,5m3 | unit | 1 |  | 0
77 | IA32A | Expanding closed vessel with the capacity up to 500 l | unit | 1 |  | 0
78 | SE53A | Pellet-based water meter with Dutch junction | unit | 1 |  | 0
78a | Company price | Thermal energy meter SHARKY 775 | unit. | 1 |  | 0
79 | IA23A | Liquid fuel filter (DOZAPHOS К700) | unit | 1 |  | 0
80 | IA23A | Liquid fuel filter (De-airing 551006D1) | unit | 1 |  | 0
81 | IA23A | Liquid fuel filter (Filter Y with flanges ) | unit | 1 |  | 0
82 | IA25B | Sludge separator for pipes in central heating system having the input nominal diameter 150 mm (mud collector) | unit | 1 |  | 0
|  | Chapter 3. Equipment |  |  |  | 0
83 | Company price | Vertical, solid biomass (briquettes) steel heating boiler with capacity Q= 100 kW, N=0.900 W | unit | 1 |  | 0
84 | Company price | Circulation pump of heating system G=4-12 M3/h, H=7-9.0m, N=0.236 kW (220V), А80/180Х М | unit | 2 |  | 0
85 | Company price | Circulation system pump G=1-1.5 m3/h, H=21m, N=0.75kW (220V), ALP2000M | unit | 2 |  | 0
86 | Company price | Two way boiler recirculation pump G=1.1-2 m3/h, H=2-3m, N=0.055kW (220V), VA25/130-2 | unit | 2 |  | 0
87 | Company price | Three way thermostatic valve D65- -D65-D50-mm | unit | 1 |  | 0
89 | Company price | Source water reservoir, V=0.5 m3 , б=1,5mm | unit | 1 |  | 0
90 | Company price | Expansion tank, V=80 l, type R2 80 275, | unit | 1 |  | 0
91 | Company price | Multi jet water meter with humid mechanism, G=1.5 m3/h, | unit | 1 |  | 0
92 | Company price | Proportional/anti-calcar dosing filter, DOSAPHOS 700 | unit | 1 |  | 0
93 | Company price | Deaerator 551006D1 | unit | 1 |  | 0
94 | Company price | Filter Y with flanges D25 | unit | 1 |  | 0
95 | Company price | Sledge collector H=700mm, | unit | 1 |  | 0
96 | Company price | Heat meter SHARKY 775 | unit | 1 |  | 0
|  | Chapter 1. Assembling works |  |  |  | 0
1 | ID05C | Lockable screw-down valve with drawer, with flange for central heating systems, with nominal D= 80...100mm (Flange Straight-way valve D80mm) equipment | unit | 2 |  | 0
2 | ID04C | Straight-way or restraint valve with sockets for central heating system with nominal D= 2" (D50) | unit | 2 |  | 0
3 | ID04A | Straight-way or restraint valve with sockets for central heating system with nominal D= 1/2" -1" (D25) | unit | 1 |  | 0
4 | ID04A | Straight-way or restraint valve with sockets for central heating system with nominal D= 1/2" -1" (D20) | unit | 10 |  | 0
5 | ID04B | Straight-way or restraint valve with sockets for central heating system with nominal D=1 1/4" -1 1/2" (D40) | unit | 1 |  | 0
6 | IA18J | Fine fittings for central heating boilers: control nozzles for fittings (nozzle D15mm for manometer) | unit | 8 |  | 0
7 | IA18J | Fine fittings for central heating boilers: control nozzles for fittings (nozzle D15mm for thermometer) | unit | 2 |  | 0
8 | ID03A | Three way valve with gland seals for central heating systems with nominal diameter 15 mm | unit | 2 |  | 0
9 | IC12E | Seamless welded or longitudinally welded steel pipe for construction, welded to distribution pipes in central heating systems for residential or social-cultural buildings, pipe having the outer diameter and wall thickness of 95 x 3,5 mm ... 108 x 4 mm (joggle F108x4 L=2.0m with 8 nozzles, 2units ) | m | 4 |  | 0
10 | IzJ13A | Sealing sheet panels connected with roving ROMTIX thermo-insulating tubes S-25mm, F108mm | m | 6 |  | 0
11 | IzJ13A | Sealing sheet panels connected with roving ROMTIX thermo-insulating tubes D 76, S=25mm, ARMOFLEX | m | 12 |  | 0
12 | IzJ13A | Sealing sheet panels connected with roving ROMTIX thermo-insulating tubes S-25mm, F57mm | m | 6 |  | 0
13 | IzJ13A | Sealing sheet panels connected with roving ROMTIX thermo-insulating tubes S-25mm, F45mm | m | 6 |  | 0
14 | IzJ13A | Sealing sheet panels connected with roving ROMTIX thermo-insulating tubes S-25mm, F32mm | m | 18 |  | 0
15 | IC11C | Black longitudinally welded steel pipe for installations, unthreaded, mounted by welding in columns, in central heating installations for residential and social-cultural buildings, the pipe having the diameter of 25х2,5mm | m | 6 |  | 0
16 | IC11F | Black longitudinally welded steel pipe for installations, unthreaded, mounted by welding in columns, in central heating installations for residential and social-cultural buildings, the pipe having the diameter of 45х2,5mm | m | 6 |  | 0
17 | IC12A | Seamless welded or longitudinally welded steel pipe for construction, welded to distribution pipes in central heating systems for residential or social-cultural buildings, pipe having the outer diameter and wall thickness of 57х3mm GOST 10704-91 | m | 4 |  | 0
18 | IC12C | Seamless welded or longitudinally welded steel pipe for construction, welded to distribution pipes in central heating systems for residential or social-cultural buildings, pipe having the outer diameter and wall thickness of 76х3mm | m | 6 |  | 0
19 | IC11C | Black longitudinally welded steel pipe for installations, unthreaded, mounted by welding in columns, in central heating installations for residential and social-cultural buildings, the pipe having the diameter of 20х2,8mm | m | 6 |  | 0
20 | IC11E | Black longitudinally welded steel pipe for installations, unthreaded, mounted by welding in columns, in central heating installations for residential and social-cultural buildings, the pipe having the diameter of 40х2,8mm | m | 4 |  | 0
21 | IC11F | Black longitudinally welded steel pipe for installations, unthreaded, mounted by welding in columns, in central heating installations for residential and social-cultural buildings, the pipe having the diameter of 50х3,2mm | m | 4 |  | 0
22 | IC12B | Black longitudinally welded steel pipe for installations, unthreaded, mounted by welding in columns, in central heating installations for residential and social-cultural buildings, the pipe having the diameter of 65х3,2mm | m | 12 |  | 0
23 | IE03A | Leak-proof (tightness) test of feeding pipelines for heating devices (aerothermal, thermal convectors, plinth convectors, etc.) at pressure, the pipe having the diameter of 3/8" ... 1" | m | 12 |  | 0
24 | IE03B | Leak-proof (tightness) test of feeding pipelines for heating devices (aerothermal, thermal convectors, plinth convectors, etc.) at pressure, the pipe having the diameter of 1 1/4" ... 2" | m | 12 |  | 0
25 | IE04B | Dilatation and contraction and functioning test of feeding pipelines for heating devices (aerothermal, thermal convectors, plinth convectors, etc.), pipe having the diameter of 1 1/4" ... 2" | m | 14 |  | 0
26 | IE03C | Dilatation and contraction and functioning test of feeding pipelines for heating devices (aerothermal, thermal convectors, plinth convectors, etc.), pipe having the diameter of 54 x 3,5 ... 83 x 3,5 mm | m | 22 |  | 0
26a | Company price | Installing manual valves, balancing and launching the internal heating system based on newly assembled heating system | system | 1 |  | 0
27 | IzA08A | Manually painted pipes with oil paint with outer diameter up to 34 mm inclusive | m | 12 |  | 0
28 | IzA08B | Manually painted pipes with oil paint with outer diameter more than 34 mm | m2 | 6.6 |  | 0
29 | IzH07A | Insulation of pipes with mineral wool or glass mats SPS 1 type, ready-made, sewed with zinc steel wire on wire mesh on one side, thickness 20; 30; 40, 50 or 60 mm, to the pipes with a circumference over thermo insulation below 35 cm, inclusive (Glass wool mats covered with metal mesh (two-sided mesh N12-1.2, brand 125) b=40mm, 0,3622м3 | m2 | 9.055 |  | 0
30 | IzI07A1 | Protection of pipe thermal insulation using 0,5 mm-thick black or zinc-coated sheets fixed with self-tapping screws with semi-round cleaved head, having the pipe circumference over the thermal insulation up to 0,35 m, assembling (Thin galvanized steel sheet S=0.5mm) | m2 | 58.632 |  | 0
31 | IzI07A2 | Protection of pipe thermal insulation using 0,5 mm-thick black or zinc-coated sheets fixed with self-tapping screws with semi-round cleaved head, having the pipe circumference over the thermal insulation up to 0,35 m, assembling | m2 | 58.632 |  | 0
32 | IC42A | Fixators and support for pipelines, boilers, devices and recipients, with the weight up to 2 kg / unit | kg | 47 |  | 0
33 | CN20B | Internal or external paint applied on metallic carpentry with enamel varnish in 2 layers including primer | m2 | 1.36 |  | 0
|  | Chapter 2. Assembling works |  |  |  | 0
34 | IA23A | Liquid fuel filter (D80) | unit | 4 |  | 0
35 | IA18A | Fine fittings for central heating boilers: thermometer (straight and corner) with protection or thermometer with round scale | unit | 2 |  | 0
36 | IA18B | Fine fittings for central heating boilers: hydrometer or manometer with control valve | unit | 2 |  | 0
37 | IA41A | Pressure releaser for central heating systems with junctions of 50 or 65 mm (Automated balancing valve) | unit | 3 |  | 0
38 | IA25C | Sludge filter for pipelines for central heating system, with nominal diameter 250 - 350 mm (Sludge collector) | unit | 1 |  | 0
|  | Chapter 3. Equipment |  |  |  | 0
39 | Company price | Round valve with flange D80 | unit | 2 |  | 0
40 | Company price | Filter Y with flange D80 | unit | 4 |  | 0
41 | Company price | Thermometer 0...150С, L=260mm | unit | 2 |  | 0
42 | Company price | Manometer P=0.01-5-6MPa | unit | 2 |  | 0
43 | Company price | Automatic thermostatic valve with sockets D25 DANFOSS, with 2 copper impulse pipes D10 set, ASV-PV/ ASV-M or similar | unit | 1 |  | 0
44 | Company price | Automatic thermostatic valve with sockets D50 DANFOSS, with 2 copper impulse pipes D10 set, ASV-PV/ ASV-M or similar | unit | 1 |  | 0
45 | Company price | Automatic thermostatic valve with sockets D40 DANFOSS, with 2 copper impulse pipes D10 set, ASV-PV/ ASV-M or similar | unit | 2 |  | 0
46 | Company price | Sludge collector H=700mm D350 | unit | 1 |  | 0
Total VAT 0 rate | [5 empty] | 0

## TMS
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Installation of biomass heating system and solar hot water production system in the kindergarten of Copceac village, Stefan Voda district
Site: | y
Section: |  | Solar hot water system
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Dismantling works |  |  |  | 0
1 | RpCI42B | Dismantling roof elements - roofing sheet, asbestos-cement, PVC, cardboard, canvas, including removing of recovering sheet (Coverage slate) | m2 | 12.4 |  | 0
2 | RpCH18A | Dismantling wood structure at waterproofing covering of stores, barracks, sheds, etc. manufactured from sawn wood ( K=0.5 carpentry) | m3 | 0.1 |  | 0
|  | Chapter 2. Construction works |  |  |  | 0
|  | Chapter 2.1. Roofing |  |  |  | 0
3 | CE41A | Assembling supporting rails with antiseptic treatment | m3 | 1.22 |  | 0
4 | CN50A | Fireproofing of wood; fixtures, arks balks, rails, wall plates | m3 | 1.22 |  | 0
|  | Chapter 2.2. Solar collector frame Кр1 |  |  |  | 0
5 | CL18A | Different metallic articles from laminate, sheet, striated sheet, poles for roof or support totally or partly inserted in concrete (position 1,2 ) | kg | 152.8 |  | 0
6 | CL18A | Different metallic articles from laminate, sheet, striated sheet, poles for roof or support totally or partly inserted in concrete (position 3,4 ) | kg | 165.96 |  | 0
7 | CL18A | Different metallic articles from laminate, sheet, striated sheet, poles for roof or support totally or partly inserted in concrete ( МС1 and МС2 ) | kg | 24.6 |  | 0
|  | Chapter 3. Assembling works |  |  |  | 0
|  | Chapter 3.1. Electric equipment |  |  |  | 0
1 | 08-03-573-4 | Suspended cabinet (panel), height, widths and length, mm, not exceeding 600х600х350 (ЩMP-2) | unit | 1 |  | 0
2 | 08-03-575-1 | Dissembled device or unit before transportation | unit | 10 |  | 0
3 | 08-03-526-1 | Automated mono-, bi-, tripolar, mounted on constructions on wall or column, power up to 25 A (VA) | unit | 2 |  | 0
|  | Chapter 3.2. Wires |  |  |  | 0
4 | 08-02-402-1 | Cable for mounted constructions and gutters by mounting the switchboard with 2-4 wires in normal environment rooms, wire section up to 10 mm2 | 100 m | 0.6 |  | 0
5 |  | Power cable VVGng-LS 3х1.5mm2 | m | 18 |  | 0
6 |  | Power cable VVGng-LS 4х1.5mm2 | m | 5 |  | 0
7 |  | Power cable VVGng-LS 5х1.5mm2 | m | 7 |  | 0
8 |  | Power cable VVGng-LS 5х2.5mm2 | m | 30 |  | 0
9 | 08-02-402-1 | Cable for mounted constructions and gutters by mounting the switchboard with 2-4 wires in normal environment rooms, wire section up to 10 mm2 | 100 m | 0.15 |  | 0
10 | 08-02-412-3 | Insert the conductors into pipes and posed metallic hoses: first mono wire or multi wire conductor in joint plait, summary section up to 16 mm2 | 100 m | 0.89 |  | 0
11 |  | Conductor PVC 2х0,75 mm2 | m | 45 |  | 0
12 |  | Conductor PVC 3х1,0 mm2 | m | 53 |  | 0
13 |  | Conductor PVC 4х1,0 mm2 | m | 6 |  | 0
|  | Chapter 3.3. Different materials |  |  |  | 0
14 | 08-02-471-4 | Vertical ground socket, round steel diameter 20 mm | 10 unit | 0.3 |  | 0
15 | 08-02-472-1 | Ground conductors: earth leakage socket, horizontal, from round steel, diameter 20 mm | 100 m | 0.11 |  | 0
16 | 08-02-472-9 | Ground conductor, open, on construction support, round steel, diameter 20 mm | 100 m | 0.1 |  | 0
17 |  | Round steel F20mm | m | 30 |  | 0
18 | 08-03-603-1 | Transformer box (ЯТП-0,25, 220/12В) | unit | 1 |  | 0
19 |  | Plastic box У409М | unit | 4 |  | 0
20 | 08-02-390-1 | Plastic channels with the width up to 40 mm (Mini channel ТМК1020) | 100 m | 0.75 |  | 0
21 |  | PVC channel (Mini channel ТМК1020) | m | 75 |  | 0
22 |  | External corner of the mini channel ТМК-YН1020 5401 | unit | 10 |  | 0
23 | 08-02-409-1 | Vinyl plast pipe on installed constructions, walls and columns, fixed with staples, diameter 16 mm | 100 m | 0.04 |  | 0
24 |  | PVH pipe D=16mm corrugated tube | m | 4 |  | 0
25 | 08-02-407-1 | Steel pipe in constructions installed on walls, fixed with staples, diameter less than 25 mm | 100 m | 0.06 |  | 0
26 |  | Steel pipe D=20х2,5mm | m | 6 |  | 0
27 |  | Metal articles | kg | 2 |  | 0
|  | Chapter 3.4. Electrical products |  |  |  | 0
28 | 08-03-591-8 | Open plug for open installation, 10А, IP44 with earth contact, with safety screen | 100 unit | 0.05 |  | 0
29 | 08-03-591-8 | Open plug for open installation, 380В, 16А, IP44 with earth contact, with safety screen | 100 unit | 0.01 |  | 0
|  | Chapter 4. General construction works |  |  |  | 0
30 | TsA16B1 | Manual digging in limited spaces, in tranches up to 4 m depth, for high tension electrical cables in ground with natural humidity without support, widths < 1 m, deepness < 1,5 m , average ground | m3 | 2.75 |  | 0
31 | TsD01B | Scatter loose soil with paddle, in uniform layers of 10-30 cm thickness in a scatter of up to 3 m from piles, including crushing the soil balls and soil from average ground | m3 | 2.75 |  | 0
32 | TsD04B | Manual punning of piles made in horizontal or inclined digging at 1/4, including watering each soil layer in part with 10 cm thickness of cohesive soil | m3 | 2.75 |  | 0
|  | Chapter 5. Equipment |  |  |  | 0
33 | Company price | Board SMP-2-0 74U2 - board with mounting panel 500x400x220, IP54 | unit | 1 |  | 0
34 | Company price | Automatic three pole switcher VA47-29/3Р/ С13 | unit | 1 |  | 0
35 | Company price | Automatic one pole switcher VA47-29/1Р/ С5 | unit | 1 |  | 0
36 | Company price | Automatic one pole switcher VA47-29/1Р/ С10 | unit | 1 |  | 0
37 | Company price | Automatic one pole switcher ВА47-29/1Р/ В5 | unit | 2 |  | 0
38 | Company price | Differentiated switcher АD 12М/2Р/10/30, 10А 30mА | unit | 1 |  | 0
39 | Company price | Differentiated switcher АD 14/4Р/10/10,10А 10mА | unit | 1 |  | 0
40 | Company price | Manual load shifting switch, three poles, 25А for 2 positions, СОМО-С-3-25 | unit | 1 |  | 0
41 | Company price | Zero Bar 8/2 | unit | 2 |  | 0
42 | Company price | Modular block terminal BZ 24 | unit | 3 |  | 0
43 | Company price | Automatic three polar switcher VA47-29/3Р/ С16 | unit | 2 |  | 0
|  | Chapter 6. Pipe joints |  |  |  | 0
1 | ID06A | Air relief valve with mobile key for central heating systems with nominal D = 1/4" (automated brass venting valve/vent pipe/D15mm ) | unit | 1 |  | 0
2 | ID04B | Straight-way or restraint valve with sockets for central heating system with nominal 1 1/4" -1 1/2" (three valve F32) | unit | 1 |  | 0
3 | ID06A | Air relief valve with mobile key for central heating systems with nominal D=10 mm) | unit | 4 |  | 0
4 | ID04A | Straight-way or restraint valve with sockets for central heating system with nominal D= 1/2" -1" (Straight-way valve with sockets D20mm, P=1.0 MPa)REHAU SOLEСT | unit | 9 |  | 0
5 | ID04B | Straight-way or restraint valve with sockets for central heating system with nominal D 1 1/4" -1 1/2" (Brass ball valveF32, Р=1MPа) | unit | 1 |  | 0
6 | ID04A | Straight-way or restraint valve with sockets for central heating system with nominal D 1/2" -1" (Brass ball valve F25, Р=1MPа) | unit | 3 |  | 0
7 | ID04A | Straight-way or restraint valve with sockets for central heating system with nominal D 1/2" -1" (Brass ball valve F20, Р=1MPа) | unit | 2 |  | 0
8 | ID04A | Straight-way or restraint valve with sockets for central heating system with nominal D 15 ( Brass ball valve F15 Ru=1,0 ) | unit | 8 |  | 0
9 | ID04A | Straight-way or restraint valve with sockets for central heating system with nominal DN 15 ( Brass ball valve F15 Ru=1,0 ) REHAU SOLEСT | unit | 2 |  | 0
10 | ID04C | Straight-way or restraint valve with sockets for central heating system with nominal D 2" (Brass ball valve F50 Ru=1,0 ) | unit | 2 |  | 0
11 | ID04A | Straight-way or restraint valve with sockets for central heating system with nominal DN 10 ( Brass ball valve F10 Ru=1,0 ) | unit | 2 |  | 0
12 | ID04A | Straight-way or restraint valve with sockets for central heating system with nominal D 1/2" -1" (brass check valve D=25 mm Ru=1MPа) | unit | 1 |  | 0
13 | ID04A | Straight-way or restraint valve with sockets for central heating system with nominal D 1/2" -1" (brass check valve D=20 mm Ru=1MPа) REHAU SOLEСT | unit | 2 |  | 0
14 | ID04C | Straight-way or restraint valve with sockets for central heating system with nominal D 2" (brass check valve D=50 mm Ru=1MPа) | unit | 1 |  | 0
15 | ID04A | Straight-way or restraint valve with sockets for central heating system with nominal D 1/2" -1" (brass check valve D=20 mm Ru=1MPа) | unit | 3 |  | 0
16 | IA20A | Screwed in safety valve with nominal D 1/2"...1" (brass spring safety valve D=15 mm Ru=1MPа ) | unit | 2 |  | 0
17 | IA20A | Screwed in safety valve with nominal D 1/2"...1" (brass spring safety valve D=20 mm Ru=1MPа Italy) REHAU SOLEСT | unit | 4 |  | 0
18 | VC24A | Elastic support of ventilator with rubber support (flexible for pump Du20) | unit | 4 |  | 0
19 | VC24A | Elastic support of ventilator with rubber support (flexible for pump Du20) REHAU SOLEСT | unit | 4 |  | 0
20 |  | Hose - flexible pipe D 20 rubber, 3х10м | m | 30 |  | 0
21 | CR03A | Wood panel made of the crushing of roundwood-shaving and wood-shaving rulers for rural constructions, executed in walls (wood beam 200х150х1000mm, 2units) | м3 | 0.06 |  | 0
|  | Chapter 7. Build-in parts for installation KIPandА |  |  |  | 0
22 | IA18J | Fine fittings for central heating boilers: control nozzles for fittings (build-in parts for thermometer ZKT-1-87) | unit | 5 |  | 0
23 | IA18J | Fine fittings for central heating boilers: control nozzles for fittings (build-in parts for manometer ZKT-275.00.90 ) | unit | 7 |  | 0
24 | ID03A | Three way valve with gland seals for central heating systems with nominal diameter 15 - 20 mm (three way valve for manometer Italy) | unit | 7 |  | 0
|  | Chapter 8. Pipelines |  |  |  | 0
25 | AcA25A | Electric welding installation of connecting steel parts in position with the diameter 50-100 mm (Cover panel F40mm) | unit | 2 |  | 0
26 | SA04E | Zinc treated steel pipe for constructions mounted in distribution pipelines in residential and social-cultural buildings having the diameter 1 1/2" , d = 40х2mm | m | 6 |  | 0
27 | SA04B | Zinc treated steel pipe for constructions mounted in distribution pipelines in residential and social-cultural buildings having the diameter 3/4", F20х2mm | m | 26 |  | 0
28 | SA04A | Zinc treated steel pipe for constructions mounted in distribution pipelines in residential and social-cultural buildings having the diameter 1/2" , F16х2mm | m | 15 |  | 0
29 | IC11D | Black steel pipe welded longitudinally for structures, non-threaded, mounted through welding in columns, in central heating system for residential and social-cultural buildings, the pipe having the diameter of 32х2,8mm | m | 12 |  | 0
30 | IC11C | Black steel pipe welded longitudinally for structures, non-threaded, mounted through welding in columns, in central heating system for residential and social-cultural buildings, the pipe having the diameter of 25х2,8mm | m | 16 |  | 0
31 | IC11B | Black steel pipe welded longitudinally for structures, non-threaded, mounted through welding in columns, in central heating system for residential and social-cultural buildings, the pipe having the diameter of 20х2,8mm | m | 9 |  | 0
32 | IC11A | Black steel pipe welded longitudinally for structures, non-threaded, mounted through welding in columns, in central heating system for residential and social-cultural buildings, the pipe having the diameter of 15х2,8mm | m | 6 |  | 0
33 | IC35A | Black steel pipe welded longitudinally for structures, non-threaded, mounted through welding in columns, in central heating system for residential and social-cultural buildings, the pipe having the diameter of 16х2,0 mm metalloplastics | m | 10 |  | 0
34 | IC35B | High-density polypropylene casted pipe installed to connect the heating bodies or devices in central heating systems with outer diameter 20х2,2 mm metalloplastics | m | 16 |  | 0
35 | IE03A | Leak-proof (tightness) test of feeding pipelines for heating devices (aerothermal, thermal convectors, plinth convectors, etc.) at pressure, the pipe having the diameter of 3/8" ... 1" | m | 98 |  | 0
36 | IE03B | Leak-proof (tightness) test of feeding pipelines for heating devices (aerothermal, thermal convectors, plinth convectors, etc.) at pressure, the pipe having the diameter of 1 1/4" ... 2" | m | 18 |  | 0
37 | IE04A | Dilatation and contraction and functioning test of feeding pipelines for heating devices (aerothermal, thermal convectors, plinth convectors, etc.), pipe having the diameter of 1 1/4" ... 2" | m | 98 |  | 0
38 | IE04B | Dilatation and contraction and functioning test of feeding pipelines for heating devices (aerothermal, thermal convectors, plinth convectors, etc.), pipe having the diameter of 54 x 3,5 ... 83 x 3,5 mm | m | 18 |  | 0
39 | IzJ13A | Sealing sheet panels connected with roving ROMTIX thermo-insulating tubes S-15mm, F16mm | m | 10 |  | 0
40 | IzJ13A | Sealing sheet panels connected with roving ROMTIX thermo-insulating tubes S-15mm, F20mm | m | 16 |  | 0
41 | IC40A | Brackets to fix steel pipes for central heating or gas heating systems, mounted by pins 1" including, PVS pins on brick walls (buckle F25) | unit | 42 |  | 0
42 | IC40B | Brackets to fix steel pipes for central heating or gas heating systems, mounted by pin 1 1/4" - 2", PVS pins on brick walls (pipe hooks , TP-5) | unit | 18 |  | 0
43 | RpCU05G | Drilling brick walls of 26 -50 cm thickness to install pipes (Wall drill F40) | unit | 6 |  | 0
44 | IC42A | Support and fixing devices for pipes, boilers, devices and recipients with weight lower than 2 kg / unit | kg | 42 |  | 0
45 | CN20B | Internal or external paint applied on metallic carpentry with enamel varnish in 2 layers including primer | m2 | 1.13 |  | 0
|  | Chapter 2. Assembling works |  |  |  | 0
46 | IA17C | Vertically mounted boiler with capacity 1000...2000 l | unit | 1 |  | 0
47 | 11-06-001-01 | Pump block, mass, kg up to: 50 (Pumping unit for solar heat collector) | unit | 2 |  | 0
48 | IA38A | Circulation pump (recirculation) mounted on the existing pipe by flanges, having a diameter up to 2 "(50 mm) including | unit | 2 |  | 0
49 | IA23A | Liquid fuel filter (Automatic deaerator) | unit | 1 |  | 0
50 | IA32A | Membrane expanding closed vessel with the capacity up to 500 l (expanding vessel) | unit | 4 |  | 0
51 | SE53A | Pellet-based water meter with Dutch junction, with diameter 20-30 mm (cold water meter) | unit | 5 |  | 0
52 | IC46D | Distributor - collector for points and heating systems mounted on readymade support (Solar heat collector ) | unit | 4 |  | 0
53 | 11-03-001-01 | Devices installed on metallic construction, panels and boards: device, mass, kg, up to: 5 (RENO Controller) | unit | 1 |  | 0
54 | 11-02-001-01 | Device installed on threaded joints, mass, kg, up to: 1,5 (electrical) | unit | 1 |  | 0
55 | 11-02-001-02 | Device installed on threaded joints, mass, kg, up to: 5 (Temperature controller, REНAU SOLEСT -SС100) | unit | 1 |  | 0
56 | 11-02-022-01 | Devices indicated primary convertors (running), installed on technological pipeline: freezing analyser, REНAU SOLEСT | unit | 1 |  | 0
57 | 11-02-001-01 | Device installed on threaded joints, mass, kg, up to: 1,5 (manometer) | unit | 7 |  | 0
58 | 11-02-001-01 | Device installed on threaded joints, mass, kg, up to: 1,5 thermometer) | unit | 5 |  | 0
59 | IA23A | Liquid fuel filter (filters) | unit | 3 |  | 0
|  | Chapter 3. Equipment |  |  |  | 0
60 | Company price | Bivalent boiler with capacity 1000/220 L Sunsystem, KSC-2 1000/220 or similar | unit | 1 |  | 0
61 | Company price | Pumping block for solar heat collector, Q=0.5-3m3/h, Р=0,7-0,8mm.c.a with electric motor N=0.23kW, Solar-3, REHAU SOLEI or similar | unit | 2 |  | 0
62 | Company price | Circulation pump for ACM system, Q=0.8-3m3/h,Р=2-6mm c.a., electric motor N=0,08кW, U=220W, | unit | 2 |  | 0
63 | Company price | Automatic deaerator code 551006D1 | unit | 1 |  | 0
64 | Company price | Expanding vessel V=60l,Р=0,6 MPа F=380mm, Н=730mm R2 060 271Р | unit | 1 |  | 0
65 | Company price | Expanding vessel V=12l, Р=0,8МРа EXTRAVAREM or similar | unit | 1 |  | 0
66 | Company price | Expanding vessel V=60l,Р=0,6 MPа F=380mm, Н=730mm Solar REHAU SOLEСT | unit | 2 |  | 0
67 | Company price | Water meter (cold water meter) F20mm | unit | 5 |  | 0
68 | Company price | Selective area solar collector S= 1,8 m2 , RENAU SOLEСT KOMBI RK 4D, REHAU SOLEСT or similar | unit | 4 |  | 0
69 | Company price | REHAU Controller or similar | unit | 1 |  | 0
70 | Company price | Electric resistance with thermal regulator, 5кW, 220V | unit | 1 |  | 0
72 | Company price | VARIO regulator or similar | unit | 1 |  | 0
73 | Company price | Temperature regulator of heating and hot water with protection system against overheating with integrated pump, REНAU SOLEСT -SС100 or similar | unit | 1 |  | 0
74 | Company price | Anti-freezing analyser, REНAU SOLEСT or similar | unit | 1 |  | 0
75 | Company price | Manometer 0-0,5 МPа | unit | 7 |  | 0
76 | Company price | Thermometer with measuring area 0 -150 Celsius degrees | unit | 5 |  | 0
77 | Company price | Support for thermometer | unit | 5 |  | 0
78 | Company price | Mechanic filter for water cleaning F20mm REHAU SOLEСT or similar | unit | 1 |  | 0
79 | Company price | Mechanic filter for water cleaning, F25mm | unit | 1 |  | 0
80 | Company price | Mechanic filter for water cleaning, F20mm | unit | 1 |  | 0
Total VAT 0 rate | [5 empty] | 0

## HV
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Installation of biomass heating system and solar hot water production system in the kindergarten of Copceac village, Stefan Voda district
Site: | y
Section: |  | Heating and ventilation
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. General construction works |  |  |  | 0
|  | Chapter 1.1. Ventilation |  |  |  | 0
1 | CL20A | Black sheet ready-to-use louvered grilles, with manually adjustable blinds, painted and embedded in walls (ventilation grille P200) | unit | 8 |  | 0
2 | CL20A | Black sheet ready-to-use louvered grilles, with manually adjustable blinds, painted and embedded in walls (ventilation grille STD 5288) | unit | 4 |  | 0
3 | IC12E | Seamless welded or longitudinally welded steel pipe for construction, welded to distribution pipes in central heating systems for residential or social-cultural buildings, pipe having the outer diameter and wall thickness of 108 x 4 mm GOST 10704-91 | m | 2 |  | 0
4 | IC12I | Seamless welded or longitudinally welded steel pipe for construction, welded to distribution pipes in central heating systems for residential or social-cultural buildings, pipe having the outer diameter and wall thickness of 159 x 4,5 mm GOST 10704-91 | m | 6 |  | 0
5 | IC12K | Seamless welded or longitudinally welded steel pipe for construction, welded to distribution pipes in central heating systems for residential or social-cultural buildings, pipe having the outer diameter and wall thickness of 219 x 6 mm GOST 10704-91 | m | 2 |  | 0
6 | IzA08B | Manual painting of pipes with oil paint, outer diameter exceeding 34 mm | m2 | 3.1 |  | 0
7 | VA02E | Manufacturing and installing straight ventilation channels from zinc or aluminium sheet of thickness 1.0 mm, with circular section perimeter of 250 - 700 mm ( air vent D125 GOST 19903-91) | m2 | 0.3 |  | 0
8 | IzJ13A | Sealing sheet panels connected with roving (thermo-insulating tubes Dinter 108, S=25mm., ARMOFLEX) | m | 2 |  | 0
9 | IzJ13A | Sealing sheet panels connected with roving (thermo-insulating tubes Dinter 125, S=25mm., ARMOFLEX) | m | 0.6 |  | 0
10 | IzJ13A | Sealing sheet panels connected with roving (thermo-insulating tubes Dinter 159, S=25mm., ARMOFLEX) | m | 6 |  | 0
11 | IzJ13A | Sealing sheet panels connected with roving (thermo-insulating tubes Dinter 219, S=25mm., ARMOFLEX) | m | 13 |  | 0
12 | IzI07A1 | Protection of pipe thermal insulation using 0,5 mm-thick black or zinc-coated sheets fixed with self-tapping screws with semi-round cleaved head, having the pipe circumference over the thermal insulation up to 0,35 m, assembling (Thin galvanized steel sheet S=0.5mm, GOST 14918-80* ) | m2 | 13 |  | 0
13 | IzI07A2 | Protection of pipe thermal insulation using 0,5 mm-thick black or zinc-coated sheets fixed with self-tapping screws with semi-round cleaved head, having the pipe circumference over the thermal insulation up to 0,35 m, assembling | m2 | 13 |  | 0
|  | Chapter 1.2. Heating |  |  |  | 0
14 | IB01A | Cast-iron radiators with free columns and circular cross-section or with connected columns and elliptical cross-section | m2 | 1.52 |  | 0
15 | IB20A | Fastening for heating body, mounted on brick wall. | unit | 8 |  | 0
16 | IzA08C | Manually painted radiators with oil paint | m2 | 1.52 |  | 0
17 | IC11C | Black steel pipe welded longitudinally for structures, non-threaded, mounted through welding in columns, in central heating system for residential and social-cultural buildings, the pipe having the diameter of 25х2,5mm GOST 10704-91 | m | 26 |  | 0
18 | IC11C | Black steel pipe welded longitudinally for structures, non-threaded, mounted through welding in columns, in central heating system for residential and social-cultural buildings, the pipe having the diameter of 20х2,8mm GOST 3262-91 | m | 2 |  | 0
19 | IE03A | Leak-proof (tightness) test of feeding pipelines for heating devices (aerothermal, thermal convectors, plinth convectors, etc.) at pressure, the pipe having the diameter of 3/8" ... 1" | m | 28 |  | 0
20 | IE04A | Dilatation and contraction and functioning test of feeding pipelines for heating devices (aerothermal, thermal convectors, plinth convectors, etc.), pipe having the diameter of 3/8" ... 1" | m | 28 |  | 0
21 | IzA08A | Manually painted pipes with oil paint, with outer diameter 34 mm inclusive | m | 28 |  | 0
22 | IC40A | Brackets to fix steel pipes for central heating or gas heating systems, mounted by pins 1" including, PVS pins on brick walls | unit | 8 |  | 0
23 | ID04A | Straight-way or restraint valve with sockets for central heating system with nominal D= 1/2" -1" (Straight-way valve with sockets D20mm ) | unit | 2 |  | 0
24 | ID04A | Straight-way or restraint valve with sockets for central heating system with nominal D= 1/2" -1" (Straight-way valve with sockets D10mm ) | unit | 4 |  | 0
25 | ID06A | Air relief valve with mobile key for central heating systems with nominal D = 1/4" (automated brass venting valve/vent pipe/D6mm) | unit | 4 |  | 0
26 | ID04A | Straight-way or restraint valve with sockets for central heating system with nominal D 1/2" -1" (thermostatic valve with sockets D20mm, with lidded thermostatic cap) | unit | 2 |  | 0
27 | VC04A | Installing mono-vacuum, anti-explosive ventilators directly with coupling device with debit 660-2.700 mc/h with electric motor of 0,8 kw | unit | 1 |  | 0
|  | Chapter 3. Equipment |  |  |  | 0
28 | Company price | Cooling ventilator D125 N=0,047kW, AIRCAPPA-125 Tekno-Point-Air or similar | unit | 1 |  | 0
Total VAT rate 0 | [5 empty] | 0

## GCW
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Installation of biomass heating system and solar hot water production system in the kindergarten of Copceac village, Stefan Voda district
Site: | y
Section: |  | General construction works
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Dismantling Works |  |  |  | 0
1 | RpCG29D | Masonry demolition through breaking by creating holes in walls | m3 | 0.13 |  | 0
2 | RpCG29D1 | Mechanical demolition of walls by creating holes in the walls | m3 | 0.52 |  | 0
3 | RpCG29D | Masonry demolition through breaking by creating holes in the walls | m3 | 0.02 |  | 0
4 | RpCG29D1 | Mechanical demolition of walls by creating holes in the walls | m3 | 0.1 |  | 0
5 | RCsB28C | Manual demolition of old concrete (dismantling of concrete foundation b= 100 mm manually) | m3 | 0.05 |  | 0
6 | RCsB28F | Mechanical demolition of old concrete (dismantling of concrete foundation b= 100 mm manually) | m3 | 0.19 |  | 0
7 | RpCO56A | Dismantling: wood carpentry - doors, 2 units | m2 | 4.62 |  | 0
8 | RpCO56A | Dismantling: wood carpentry - window, 1 unit | m2 | 2.86 |  | 0
9 | RpCJ35A | Unpacking of interior or exterior plaster on walls or ceilings. Removing plaster from ceilings | m2 | 32.8 |  | 0
10 | RpCJ35A | Unpacking of interior or exterior plaster on walls or ceiling. Removing plaster from walls | m2 | 79.2 |  | 0
11 | RpCB18B | Manual dissembling of old concrete, foundations and elevations with concrete dosage over 50 kg/mc. Manual dissembling of concrete foundation | m3 | 0.07 |  | 0
12 | RpCB18F | Mechanical dissembling of old concrete, simple concrete. Mechanical dissembling of old concrete foundations | m3 | 0.29 |  | 0
|  | Chapter 2. Construction works |  |  |  | 0
|  | Chapter 2.1. Gaps |  |  |  | 0
|  | Chapter 2.1.1. Windows |  |  |  | 0
13 | CK23B | Plastic windows with one or more wings in constructions of up to 35 m height, with area frame between 1,00 and 2,5 mp inclusive | m2 | 4.14 |  | 0
14 | CK07A | Wood windowsills up to 30 cm widths installed in wood windows | m | 2.3 |  | 0
15 | CE23B3 | Zinc steel sills and blinds of 0,5 mm thickness on a bitumen cardboard installed on a balancing lice-cement mortar platform M 100-T, fastened on brick walls for smaller or equal then 2 m, width 16 - 30 cm | m | 2.3 |  | 0
|  | Chapter 2.1.2. Doors |  |  |  | 0
16 | CK12A | Metallic doors manufactured from laminated steel, cold fastened steel profiles, including the fittings and accessories necessary for doors installed in masonry of any type construction with a height of 35 m inclusive, in a wing, with frame area of up to 7 mp inclusive (thermo insulating metallic door) | m2 | 2.1 |  | 0
|  | Chapter 2.2. Treating the door cavity |  |  |  | 0
17 | RpCU05G | Performing perforation for pipelines or drilling in brick walls of 26 -50 cm thickness (bearing-out masonry ) | unit | 2 |  | 0
18 | RCsB21B к=0,24 | Mechanical drilling of 5 cm diameter holes in concrete of 25 cm thickness ( k=0,24 ) | unit | 29 |  | 0
19 | CL18A | Different metallic articles from laminate, sheet, striated sheet, poles for roof or support totally or partly inserted in concrete (installing the beam position 1) | kg | 48.28 |  | 0
20 | RpCU08B | Adhesive layers, made with cement priming in one layer | m2 | 0.54 |  | 0
21 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, fully or partially embedded in concrete (L-steel p. 2,3 ) | kg | 110.18 |  | 0
22 | CC03B | Mounting of welded nets at heights less than or equal to 35 m, in walls and diaphragms, weighing more than 3 kg / m (p 4) | kg | 28.67 |  | 0
23 | CC02B | Concrete reinforced fittings OB 37 shaped in site workshops, with bar diameter over 8 mm, inclusively, and embedded in beams and poles at height less or equal to 35 m, excluding constructions made with sliding formwork (reinforced fittings p. 5,6,7,8) | kg | 11.56 |  | 0
24 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, fully or partially embedded in concrete (slabs p.9) | kg | 17.92 |  | 0
|  | Chapter 2.3. Brick fitting in the existing cavity |  |  |  | 0
25 | CD50A | Single brick masonry, format 250 x 120 x 65 for external walls of 4 m height | m3 | 0.76 |  | 0
26 | CC02K | Concrete reinforced fittings OB 37 shaped in site workshops, with bar diameter over 8 mm inclusively, and embedded in beams and poles at height less or equal to 35 m, excluding constructions made with sliding formwork | kg | 6.67 |  | 0
|  | Chapter 2.4. Flooring |  |  |  | 0
27 | TsC54C | Foundation made of gravel, gr.40 mm | m3 | 1.31 |  | 0
28 | CG22A k=1.7 | Concrete flooring class C 10/8 (Bc 10/B 150) of 10 cm thickness, in a continuous field, scrubbed, cast in place, in rooms with a surface of more than 16 sq.m. (Support layer of B7.5. gr. 170mm ) | m2 | 32.8 |  | 0
29 | CG01A | Support flooring layer made of cement mortar M 150-T of 3 cm thickness with finely plastered surface | m2 | 32.8 |  | 0
30 | CG17D | Ceramic sheet flooring including support layer of adhesive mortar made on surfaces more than 16 m2 | m2 | 32.8 |  | 0
|  | Chapter 2.5. Internal finishing |  |  |  | 0
31 | RpCJ18B | Finishing with internal plastering of 3 mm thickness made with plaster paste (ceilings) | m2 | 32.8 |  | 0
32 | CN01A | Simple painting with whitewash made on support surface in two layers of whitewash (ceilings) | m2 | 32.8 |  | 0
33 | CF02B | Internal plastering of 2 cm thickness, manually evened on walls and poles, plane surfaces with lime-cement mortar M 100-T for spritzer, prime, and visible layer on brick masonry or small concrete blocks (with reveals ) | m2 | 82.71 |  | 0
34 | CN01A | Simple painting with whitewash made on support surface in two layers of whitewash (walls with reveals) | m2 | 82.71 |  | 0
|  | Chapter 2.6. Platform for equipment |  |  |  | 0
35 | TsA02B | Manual soil digging in limited spaces under 1,00 m or over 1,00 m widths, executing without support on vertical banks at foundations, channels, basements, drainage, combining steps, in uncohesive or slightly cohesive soil at the depth of < 0,75 m middle soil | m3 | 0.72 |  | 0
36 | CA03G | Concrete poured in foundations, basements, support walls, prepared by site concrete-mixer and poured with classical means of concrete procured from stations according to. art. CA01 and poured with classical means, concrete of type .... B15 | m3 | 1.2 |  | 0
37 | CB02A | Encasements made out of reusable panels with boarding made out of short and sub-short soft timber to pour concrete in bearings, glass-shaped foundations and equipment foundations, including supports | m2 | 0.92 |  | 0
38 | CC03A | Mounting welded net at height smaller or equal to 35 m, on walls and diaphrgmas with weight of nets less than 3 kg/mp per net | kg | 13.88 |  | 0
39 | TsD01B | Scattering with the spade the loose soil, in uniform layers of 10-30 cm thick for a scattering of up to 3 m prom piles, including by breaking the balled roots from the middle soil | m3 | 0.72 |  | 0
|  | Chapter 2.7. Smoke chimney |  |  |  | 0
40 | CA07A k=2.5 | Preparation and pouring of concrete class C25/20 (Bc 25/ B 330) or C 30/25 (Bc 30/ B 400) in subpouring of 20 mm thickness for technological equipment and metallic poles (pouring concrete under metallic support М200, k=2,5) | m2 | 2.25 |  | 0
41 | CL08A | Metallic elements (pillars, beams, farms) ready-made, delivered completely assembled, mounted on the construction site, in the structure of light construction (stack saddle) | t | 1.03 |  | 0
42 | IC41C | Brackets to fix steel pipes to install central or gas heating systems, mounting through shooting, pipe having the diameter 1/2" - 4" screws М16 | unit | 12 |  | 0
36 | company price | Double sided chimney, stainless steel sheet, insulation S = 50mm of density mineral wool 185kg/m3, inner diameter 300mm, H=14m, | set | 1 |  | 0
43 | CN20B | Interior or exterior painting applied in 2-layer alkyd-metallic metalworking including primer | m2 | 27.8 |  | 0
|  | Chapter 2.7.2. Smoke chimney foundation |  |  |  | 0
45 | TsA02B | Manual digging in limited spaces smaller than 1,00 m or more than 1,00 m width, made without support, with vertical banks, on foundations, channels, basements, drainage channels, twinning steps, in non-cohesive or slightly cohesive soil at the depth of < 0,75 m middle soil | m3 | 15.03 |  | 0
46 | CA02B | Ordinary concrete poured in leveling, slopes at heights of up to 35 m inclusive, manufactured by concrete plants or ready-made concrete as per Item CA01, poured with classical means C 10/8 (Bc 7,5 ) | m3 | 1.1 |  | 0
47 | CA03G | Reinforced concrete poured in foundations, footings, retaining walls, walls below zero-level, manufactured by concrete plants or ready-made concrete as per Item CA01, poured with classical means, reinforced concrete of Class... В 15 | m3 | 6.9 |  | 0
48 | CB02A | Encasements made out of reusable panels with boarding made out of short and sub-short soft timber to pour concrete in bearings, glass-shaped foundations and equipment foundations, including supports | m2 | 11.4 |  | 0
49 | CC02I | Steel-reinforced concrete OB 37 shaped at on-site workshops, with bar diameter up to 8mm inclusive mounted in walls and diaphragms at height less or equal to 35 m, excluding the constructions executed with reusable panels | kg | 29.19 |  | 0
50 | CC02B | Steel-reinforced concrete OB 37 shaped at on-site workshops, with bar diameter more than 8mm mounted in walls and diaphragms, excluding the constructions executed with reusable panels | kg | 120.14 |  | 0
51 | CC02L | Steel-reinforced concrete OB 37 shaped at on-site workshops, with bar diameter more than 8mm mounted in beams and poles at heights smaller or equal to 35 m, excluding the constructions executed with reusable panels (wall dowel А1) | kg | 45.24 |  | 0
52 | TsD01B | Scattering with the spade the loose soil, in uniform layers of 10-30 cm thick for a scattering of up to 3 m prom piles, including by breaking the balled roots from the middle soil | m3 | 9.5 |  | 0
53 | TsD04A | Manual punning of horizontal or 1/4 inclined digging, including watering each soil layer in part with 10 cm thick uncohesive soil (packing ) | m3 | 9.5 |  | 0
54 | TsD01B | Scattering with the spade the loose soil, in uniform layers of 10-30 cm thick for a scattering of up to 3 m prom piles, including by breaking the balled roots from the middle soil | m3 | 5.54 |  | 0
|  | Chapter 2.8. Drainage |  |  |  | 0
55 | TsC03F1 | Mechanical excavation with an excavator of 0,40-0,70 mc, with internal combustion engine and hydraulic control, in ground with natural humidity, discharge into land category II (soil excavation, loading into vehicles) | 100 m3 | 0.06 |  | 0
56 | TsA20B | Manual digging, on slopes, following the mechanical excavation or scraper digging, to complete the digging at the slope profile, in middle-level ground (manual fine digging of 10% of total volume due to existing close by building) | m3 | 0.57 |  | 0
57 | TsI50A | Transporting the load with trucks up to 1 km distance | t | 11.5 |  | 0
58 | TsC03F1 | Mechanical excavation with an excavator of 0,40-0,70 mc, with internal combustion engine and hydraulic control, in ground with natural humidity, discharge into land category II (soil excavation, loading into vehicles) | 100 m3 | 0.03 |  | 0
59 | TsI50A | Transporting the load with trucks up to 1 km distance | t | 5.42 |  | 0
60 | TsD01B | Scattering with the spade the loose soil, in uniform layers of 10-30 cm thick for a scattering of up to 3 m prom piles, including by breaking the balled roots from the middle soil (manual back fill) | m3 | 3.1 |  | 0
61 | TsD04A | Manual punning of horizontal or 1/4 inclined digging, including watering each soil layer in part with 10 cm thick uncohesive soil (hand punned) | m3 | 3.1 |  | 0
62 | TsC50B | Natural road reparation and maintenance after soil transportation for each 0,5 km, soil category II (road reparation and maintenance for 1 km к=2) | 100 m3 | 0.03 |  | 0
63 | TsC54A | Sand layer foundation (sand cushion, thickness 100mm) | m3 | 0.23 |  | 0
64 | AcD51A | Prefabricated sewer chimney Dn 1,0 m, on site without underground waters (drainage well D=1,0 m.) | m3 | 0.78 |  | 0
65 | AcD53A1 | Prefabricated reinforced cast elements of drainage chimneys, circulating (ring) with diameter 1.0 m, for sewage on site without underground water | м2 | 1 |  | 0
66 | CG22A1 | Simple concrete flooring of Class C 10/8 (Bc 7.5/B 150), 10 cm thick, in jointless field, levelled, cast in place, in premises with surface area larger than 16 m2 (thickness - 8 cm) (concrete class В10, thickness 260mm, K=2,6 ) | m2 | 0.79 |  | 0
67 | AcE07A | Mounting iron or cast iron lids without support part to drainage channels of water and sewage installations, outside road type I (cast iron lid ) | unit | 1 |  | 0
68 | IC44A | Manufacture, mounting, and cementing the protection pipelines through walls, pipe with diameter 1" -2" (pressure seal Du=150mm, L=200mm) | unit | 1 |  | 0
69 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, all or partially embedded in concrete | kg | 41.1 |  | 0
70 | IzF18B | Equalisation support layer or insulation protection layer, including related mouldings executed with ready made mortar cement M100-T without lime, plastered on horizontal or inclined surfaces up to 40 %, applied as a 2 cm layer (trowel finish of inside with concrete with plastering) | m2 | 6.4 |  | 0
71 | IzF04F | Horizontal layer executed inside for terraces, roofs or foundations and radiation in soils without ground waters including slopes and dips in a current hydro insulation of inclined areas of 40% or vertical planes or curbs with bitumen or bitumen with rubber addition, applied with the brush or rubber gauge (purlin) (bitumen side hydro insulation 2 times | m2 | 9.54 |  | 0
72 | RCsB21A | Mechanic digging of holes of 5 cm diameter in concrete with thickness up to 20 cm ( h-om =0.5 ) | unit | 5 |  | 0
|  | Chapter 2.9. Additional works |  |  |  | 0
|  | Chapter 2.9.1. Dome К-1 |  |  |  | 0
73 | CL18A | Various metallic accessories made out of rolled tubes, plates, dashed plates, reinforced concrete, support or cover tubes, totally or partially embedded in concrete (Dome construction К-1) | kg | 57.2 |  | 0
74 | CN20A | Internal and external painting with oil paint on metallic carpentry in 3 layers | m2 | 1.54 |  | 0
75 | CE30A | Domes on roofs or tile coverage, eternal type plates, etc. of raw wood boards (24 mm thickness), in regular constructions. Resource norms with 0 (zero) value are taken in accordance with the project. (roof boarding) | m2 | 2.8 |  | 0
76 | CN51A | Antiseptic treatment of wood on hidden surfaces with antiseptic pills: pillars, arcs, beams. (timber treatment) | m3 | 0.03 |  | 0
77 | CN50A | Timber fireproofing; pillars, arcs, beams, rails, plates. (fireproofing) | m3 | 0.03 |  | 0
78 | CE31A1 | Shaped boards for gutter or fronton made of sanded boards (trimming ) | m2 | 3.1 |  | 0
79 | CN17A | Painting with enamel and alkyd resins-based paints applied on wood carpentry in 2 layers of alkyd enamel including prime (painting of lining) | m2 | 3.1 |  | 0
80 | CE07A | Sheet metal roofing tiles (Lindab type) | m2 | 3.9 |  | 0
|  | Chapter 2.9.2. КР-1 and ramp |  |  |  | 0
81 | TsA02B | Manual digging in limited spaces smaller than 1,00 m or more than 1,00 m width, made without support, with vertical banks, on foundations, channels, basements, drainage channels, twinning steps, in non-cohesive or slightly cohesive soil at the depth of < 0,75 m middle soil | m3 | 4 |  | 0
82 | TsC54C | Gravel layer foundation | m3 | 0.11 |  | 0
83 | CA02C | Ordinary concrete poured in foundations, footings, retaining walls, walls at 35 m height, manufactured by concrete mixture as per Item CA01, poured with classical means, В 7.5 b=200 mm (for foundation) | m3 | 0.6 |  | 0
84 | CA03G | Ordinary concrete poured in foundations, footings, retaining walls, walls below zero-level, manufactured by concrete plants or ready-made concrete as per Item CA01, poured with classical means, reinforced В 15 | m3 | 3.3 |  | 0
85 | CB02A | Encasements made out of reusable panels with boarding made out of short and sub-short soft timber to pour concrete in bearings, glass-shaped foundations and equipment foundations, including supports | m2 | 19.04 |  | 0
86 | CC01A | Concrete reinforced fittings OB 37 shaped in site workshops, with bar diameter over 8 mm, inclusively | kg | 10.71 |  | 0
87 | CC01B | Concrete reinforced fittings OB 37 shaped in site workshops, with bar diameter over 8 mm, inclusively | kg | 74.04 |  | 0
88 | TsD01B | Scattering with the spade the loose soil, in uniform layers of 10-30 cm thick for a scattering of up to 3 m prom piles, including by breaking the balled roots from the middle soil | m3 | 1.81 |  | 0
89 | TsD04A | Manual punning of horizontal or 1/4 inclined digging, including watering each soil layer in part with 10 cm thick uncohesive soil | m3 | 1.81 |  | 0
90 | TsD01B | Scattering with the spade the loose soil, in uniform layers of 10-30 cm thick for a scattering of up to 3 m prom piles, including by breaking the balled roots from the middle soil (manual scattering of extra prime) | m3 | 2.19 |  | 0
91 | CG01A | Cement concrete flooring support layer M 150-T of 3 cm thickness finely plastered | m2 | 3.64 |  | 0
92 | CL18A | Various metallic accessories made out of rolled tubes, plates, dashed plates, reinforced concrete, support or cover tubes, totally or partially embedded in concrete railing ОG1 | kg | 12.29 |  | 0
93 | CL18A | Various metallic accessories made out of rolled tubes, plates, dashed plates, reinforced concrete, support or cover tubes, totally or partially embedded in concrete railing ОG2 | kg | 12.29 |  | 0
94 | CL18A | Various metallic accessories made out of rolled tubes, plates, dashed plates, reinforced concrete, support or cover tubes, totally or partially embedded in concrete railing ОG3 | kg | 11.94 |  | 0
95 | CN20B | Interior or exterior painting applied in 2-layer alkyd-metallic metalworking including primer | m2 | 0.99 |  | 0
Total VAT 0 rate | [5 empty] | 0

## EEF
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Installation of biomass heating system and solar hot water production system in the kindergarten of Copceac village, Stefan Voda district
Site: | y
Section: |  | Electricity and lighting
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Assembling works |  |  |  | 0
|  | Chapter 1.1. Electrical equipment |  |  |  | 0
1 | 08-03-526-1 | Automated mono-, bi-, tripolar, mounted on constructions on wall or column, power up to 25 A | unit | 1 |  | 0
2 | 08-01-081-2 | Control and signalling device (button, control key, electromagnetic blocking lock, acoustic signal, signalling lamp) quantities connected to 6 (speed controller) | unit | 1 |  | 0
3 | 10-08-002-04 | Automatic OS warning devices: contact, magnetic contact when opening the windows, doors (Sensor controller DD-009) | unit | 1 |  | 0
|  | Chapter 1.2. Illumination equipment |  |  |  | 0
4 | 08-03-594-1 | Light source with luminescent tubes, mounted separately on pivot points, number of tubes in the light source, 1 | 100 unit | 0.09 |  | 0
5 |  | Light source, ЛCП44- 1х18 -002 IP65 | unit | 7 |  | 0
6 |  | 10 | unit | 7 |  | 0
7 |  | Starter 80C-220 | unit | 7 |  | 0
8 |  | Light source ЛБО 054 Econom 1x18-112 | unit | 2 |  | 0
9 |  | Light bulbs 8Вт T5 G5 1х8 | unit | 2 |  | 0
10 |  | Battery operated flash | unit | 1 |  | 0
11 | 08-02-144-1 | Connecting the wires or cables to clamps, section up to 2,5 mm2 (emergency power unit BAP AWEx LE 58/3) | 100 unit | 0.01 |  | 0
12 |  | Emergency power unit BAP AWEx LE 58/3 | unit | 1 |  | 0
|  | Chapter 1.3. Cable |  |  |  | 0
13 | 08-02-402-1 | Cable for mounted constructions and gutters by mounting the switchboard with 2-4 wires in normal environment rooms, wire section up to 10 mm2 | 100 m | 1.07 |  | 0
14 | 08-02-412-3 | Introduce the cable in pipes and posed metallic hoses: first mono- or multi-wire conductor in common joint plait, summary section up to 16 mm2, | 100 m | 2.01 |  | 0
15 |  | Power cable VVGng-LS 3х1.5mm2 | m | 126 |  | 0
16 |  | Power cable VVGng-LS 4х1.5mm2 | m | 15 |  | 0
17 |  | Power cable VVGng-LS 5х1.5mm2 | m | 15 |  | 0
18 |  | Power cable VVGng-LS 5х2.5mm2 | m | 45 |  | 0
|  | Chapter 1.4. Other materials |  |  |  | 0
19 | 08-02-471-4 | Vertical ground socket, round steel diameter 20 mm | 10 unit | 0.3 |  | 0
20 | 08-02-472-1 | Ground conductors: earth leakage socket, horizontal, from round steel, diameter 20 mm | 100 m | 0.11 |  | 0
21 | 08-02-472-9 | Ground conductor, open, on construction support, round steel, diameter 20 mm | 100 m | 0.15 |  | 0
22 |  | Round steel F20mm | m | 35 |  | 0
23 | 08-02-472-6 | Ground conductor, open, on construction support, sheet steel, section 100 mm2 (flat steel 25*4mm ) | 100 m | 0.35 |  | 0
24 | 08-03-603-1 | Transformer box (ЯТП-0,25, 220/12В) | unit | 1 |  | 0
25 |  | Connection box У409М | unit | 6 |  | 0
26 | 08-02-409-1 | Vinyl plast pipe on installed constructions, walls and columns, fixed with staples, diameter 16 mm | 100 m | 0.11 |  | 0
27 |  | PVH pipe D=16mm corrugated tube | m | 11 |  | 0
28 | 08-02-390-1 | Plastic channels with the width up to 40 mm (Mini channel ТМК1020) | 100 m | 1.07 |  | 0
29 |  | PVC channel (Mini channel ТМК1020) | m | 107 |  | 0
30 |  | External corner channel ТМК-YН1020 5401 | unit | 10 |  | 0
31 | 08-03-575-1 | Dismantled device or equipment prior to transportation | unit | 1 |  | 0
32 | 08-03-573-4 | Suspended cabinet (deskstand), height, width and depth, mm, (transfer box 600х600х350 (main grounding bus SZ-Z-30УХЛ3/ГЗШ-8/ cabinet 250х350х170mm) | unit | 1 |  | 0
33 |  | Ground connection (main grounded bus ШЗ-3-30УХЛ3/ГЗШ-8/ cabinet 250х350х170mm, 8 clamps for 275А) | unit | 1 |  | 0
34 | 08-02-302-1 | Steel cable transformer length up to 30 m | unit | 1 |  | 0
35 |  | Zinc cable, Ф8,3mm | m | 26 |  | 0
36 | 08-02-152-6 | Metallic construction weighing less than 4 kg (tubular mast К987У3) | 100 units | 0.02 |  | 0
37 |  | Tension packing (stretching socket) К804У3 | unit | 2 |  | 0
38 |  | Cable support parts (cable bracket) | unit | 13 |  | 0
39 |  | Metallic articles | kg | 5 |  | 0
|  | Chapter 1.5. Electrical products |  |  |  | 0
40 | 08-03-591-4 | Two button switch in open installation 16А, 220А IP44 | 100 units | 0.04 |  | 0
41 | 08-03-591-8 | Open socket in open installations , 220В, 16А, IP44 with earth connection | 100 units | 0.02 |  | 0
|  | Chapter 2. General construction works |  |  |  | 0
42 | TsA16B1 | Manual digging in limited spaces, in tranches up to 4 m depth, for high tension electrical cables in ground with natural humidity without support, widths < 1 m, deepness < 1,5 m , middle soil | m3 | 2.75 |  | 0
43 | TsD01B | Scatter loose soil with paddle, in uniform layers of 10-30 cm thickness in a scatter of up to 3 m from piles, including crushing the soil balls and soil from middle soil | m3 | 2.75 |  | 0
44 | TsD04B | Manual punning of piles made in horizontal or inclined digging at 1/4, including watering each soil layer in part with 10 cm thickness of cohesive soil | m3 | 2.75 |  | 0
|  | Chapter 3. Equipment |  |  |  | 0
454A | company price | Electricity generator with DIESEL motor, capacity 2,9kVA, 220V/50Hz, equipped with automatic connection block to power | set | 1 |  | 0
45 | company price | Automatic three pole switch ВА47-29/3Р/ С16 | unit | 1 |  | 0
46 | company price | Speed regulator for vacuum ventilator, RVN | unit | 1 |  | 0
47 | company price | Movement sensor with timer 5...480c), ~230В, IP44 DD-009 | unit | 1 |  | 0
Total VAT 0 rate | [5 empty] | 0

## ATM
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Installation of biomass heating system and solar hot water production system in the kindergarten of Copceac village, Stefan Voda district
Site: | y
Section: |  | Automated control and regulation system
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Assembling works |  |  |  | 0
|  | Chapter 1.1. Panels |  |  |  | 0
1 | 11-06-001-02 | Panel, mass, kg, up to: 100 (Switchboard and alarm ЩУС- board type ЩМП-4 ) | unit | 1 |  | 0
2 | 11-03-001-01 | Devices installed on metallic constructions, panels and desk stands: device, mass, kg up to: 5 (brand equipment inserted in board ЩУС ) | unit | 38 |  | 0
3 | 11-08-001-04 | Joining electrical grids to devices by soldering | 100 units | 0.76 |  | 0
4 | 08-03-575-1 | Dismantled device or fitting prior to transportation (installing the equipment of EL brand in the board ЩУС) | unit | 35 |  | 0
5 | 11-08-001-04 | Connecting the power grids to devices by means of adhesion/soldering | 100 unit | 0.7 |  | 0
6 | 11-06-002-01 | Electrical grids in boards and desk stands: cabinet and board (wiring PV1 1х1,5) | 100 m | 0.8 |  | 0
7 | 11-06-002-01 | Electrical grids in boards and desk stands: cabinet and board (wiring PV3 1х1,5) | 100 m | 0.7 |  | 0
|  | Chapter 2. Equipment |  |  |  | 0
8 | Company price | Panel ЩМП-4 - board 800х650х250, IP54 | unit | 1 |  | 0
9 | Company price | Universal switch (number written on plug -23). УП5312-С86 | unit | 2 |  | 0
10 | Company price | SwitchALCLR-22-3 | unit | 5 |  | 0
11 | Company price | Control key 'mushroom', AЕА -22 | unit | 2 |  | 0
12 | Company price | Intermediate relay, 220V ПЭ37-44У3 | unit | 11 |  | 0
13 | Company price | Intermediate relay, 220V, ПЭ37-62У3 | unit | 2 |  | 0
14 | Company price | Time switch РКВ11-33-11УХЛ4, 220V | unit | 2 |  | 0
15 | Company price | Light signal fitting АD-22DS | unit | 13 |  | 0
16 | Company price | Diode D226B | unit | 14 |  | 0
17 | Company price | Bell ZD-47 | unit | 1 |  | 0
18 | Company price | Three pole switch VN-32/3/20 | unit | 1 |  | 0
19 | Company price | Automatic 1 button switch ВА47-29/1Р/ С5 | unit | 11 |  | 0
20 | Company price | Automatic 1 button switchВА47-29/1Р/ С8 | unit | 1 |  | 0
21 | Company price | Automatic 1 button switch ВА47-29/1Р/ В5 | unit | 3 |  | 0
22 | Company price | Differentiated switch АД 12М/2Р/10/30, 10А 30мА | unit | 1 |  | 0
23 | Company price | Commutator (shunt trip), РН47 | unit | 1 |  | 0
24 | Company price | Small scale switch 230V, 9А, КМИ -10910 | unit | 5 |  | 0
25 | Company price | Contact add-on adapter ПКИ-40 | unit | 5 |  | 0
26 | Company price | Electro-thermic relay RTI -1302 | unit | 1 |  | 0
27 | Company price | Electro-thermic relay RTI -1306 | unit | 2 |  | 0
28 | Company price | Electro-thermic relay RTI -1308 | unit | 2 |  | 0
29 | Company price | Light indicator, 380V | unit | 1 |  | 0
30 | Company price | Outdoor socket with ground contact 220V 10А | unit | 1 |  | 0
31 | Company price | Zero bus 8/2 | unit | 2 |  | 0
32 | Company price | Clamp block BZ 24 | unit | 10 |  | 0
|  | Chapter 1.1. Automatic equipment |  |  |  | 0
1 | 11-02-001-01 | Device installed by a junction of flanges, weight, in kg, up to: 1,5 (thermometer) | unit | 4 |  | 0
2 | 11-02-001-01 | Device installed by a junction of flanges, weight, in kg, up to: 1,5 (heat converter ТС ) | unit | 1 |  | 0
3 | 11-06-001-01 | Panel, mass, kg up to: 50 (indicator regulator with PID legal regulation, switchboard) | unit | 1 |  | 0
4 | 11-02-001-01 | Device installed by a junction of flanges, weight, in kg, up to: 1,5 (Manometer DM2010Сг) | unit | 4 |  | 0
5 | 11-02-001-01 | Device installed by a junction of flanges, weight, in kg, up to: 1,5 (Manometer) | unit | 15 |  | 0
6 | 11-03-001-01 | Devices installed on metallic constructions, panels and desk stands: device, mass, kg up to: 5 (relay sensors of level ROS-301) | unit | 1 |  | 0
7 | 08-01-081-1 | Control and signalling device (button, control key, electromagnetic blocking lock, acoustic signal, signalling lamp), quantity of connected units up to 2 (gas contamination alarm (СО). Seitron RGD CO) | unit | 0 |  | 0
|  | Chapter 1.2. Electrical equipment |  |  |  | 0
8 | 08-03-532-4 | Desk switch with buttons of general use installed on wall or column, quantity of switch elements not more than 3 | unit | 5 |  | 0
9 | 08-03-575-1 | Dismantled device or fitting prior to transportation | unit | 10 |  | 0
|  | Chapter 1.3. Pipe joints |  |  |  | 0
10 | ID04A | Straight-way or restraint valve with sockets for central heating system with nominal diameter 1/2" (Three valve, 14М1-16 ) | unit | 19 |  | 0
|  | Chapter 1.4. Cables and wires |  |  |  | 0
11 | 08-02-402-1 | Cable in constructions embedded and drainpipes embedded in switchboards with 2-4 wires, in rooms with normal environment, wire section up to 10 mm2 | 100 m | 0.31 |  | 0
12 | 08-02-412-2 | Insert conductors in metallic pipes and hoses posed: mono- or multi-wire conductor in joint net, Summary section of 6 mm2 | 100 m | 0.71 |  | 0
13 |  | Control cable KVVGng- LSLTx 4х1,0mm2 | m | 34 |  | 0
14 |  | Control cable KVVGng- LSLTx 5х1,0mm2 | m | 127 |  | 0
15 |  | Control cable KVVGng- LSLTx 7х1,0mm2 | m | 13 |  | 0
16 | 08-02-158-4 | Dry control end cap, section of conductor up to 2,5 mm2, quantity of conductors up to: 4 (cable end sealing) | unit | 8 |  | 0
17 | 08-02-158-5 | Dry control end cap, section of conductor up to 2,5 mm2, quantity of conductors up to: 7 | unit | 24 |  | 0
|  | Chapter 1.5. Protection |  |  |  | 0
18 | 08-02-411-1 | Metallic hose, outer diameter up to 48 mm, flexible (flexible water hose Du15, РЗ-ЦХ-Ш) | 100 m | 0.05 |  | 0
|  | Chapter 1.6. Impulse |  |  |  | 0
19 | 11-06-002-04 | Electrical grids through tubes in switchboards and desk stands: steel tubes | 100 m | 0.095 |  | 0
20 |  | Steel pipe D=18х1,2mm GOST10704-91 | m | 9.5 |  | 0
|  | Chapter 1.7. Additional materials |  |  |  | 0
21 | 08-02-390-1 | Plastic channels of up to 40 mm widths (Mini-channels ТМК1020) | 100 m | 0.53 |  | 0
22 |  | PVC channel (mini-channel ТМК 1020) | m | 36 |  | 0
23 |  | PVC channel (mini-channel ТМК 1720) | m | 17 |  | 0
24 | 08-02-409-1 | Vinyl plast pipe on installed constructions, walls and columns, fixed with staples, diameter 16 mm | 100 m | 0.04 |  | 0
25 |  | PVH pipe D=16mm corrugated tube | m | 4 |  | 0
26 |  | Connecting cassette ТМК-AD70 5402 | unit | 3 |  | 0
27 | 08-02-406-1 | Metallic constructions | t | 0.01 |  | 0
|  | Chapter 2. Equipment |  |  |  | 0
28 | Company price | Thermometer 0...120С | unit | 4 |  | 0
29 | Company price | Thermal resistance (thermoelement -50...+150'C., length 26mm, with extra cable 5m), ТС 034-50М.B3.26/5 "OVEN" | unit | 1 |  | 0
30 | Company price | Device to measure - regulate for -50...+200*С, 50М switchboard), OVEN ТРМ12А-Щ1-ТС-0,25-К | unit | 1 |  | 0
32 | Company price | Manometer measuring 0...0,25MPа | unit | 9 |  | 0
33 | Company price | Manometer measuring 0...0,4MPа | unit | 6 |  | 0
34 | Company price | Level sensor relay with 2 levels, РОС-301 | unit | 1 |  | 0
35 | Company price | Gas alarm (СО)). Seitron RGD CO | unit | 1 |  | 0
37 | Company price | Control key Start, Stop. SB-7 | unit | 10 |  | 0
38 | Company price | Key case КП102 | unit | 5 |  | 0
Total VAT 0 rate | [5 empty] | 0

## BK
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Installation of biomass heating system and solar hot water production system in the kindergarten of Copceac village, Stefan Voda district
Site: | y
Section: |  | Water supply and sewage
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
0
0
Total VAT 0 rate | [5 empty] | 0

## SIP
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Installation of biomass heating system and solar hot water production system in the kindergarten of Copceac village, Stefan Voda district
Site: | y
Section: |  | Fire safety system
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Assembling works |  |  |  | 0
1 | 10-08-001-02 | Automatic fire detector "ПС": reception, control and launch. Concentrator: main block for 20 rayons (Fire alarm control unit "Варта-1/832") | unit | 1 |  | 0
2 | 08-01-080-1 | Device to measure and protection, number of connectors up to 2 (Relay RM1 ) | unit | 1 |  | 0
3 | 10-08-002-02 | Automatic fire detector "ПС": smoke, photoelectric, radioisotope, light in normal operation (ИП) | unit | 6 |  | 0
4 | 10-08-002-02 | Automatic fire detector "ПС": smoke, photoelectric, radioisotope, light in normal operation (ИПР) | unit | 2 |  | 0
5 | 10-04-066-05 | Wall devices: warning and light alarm, 12В SA-913F | unit | 1 |  | 0
6 | 08-02-402-1 | Cable in constructions embedded and drainpipes embedded in switchboards with 2-4 wires, in rooms with normal environment, wire section up to 10 mm2 | 100 m | 0.27 |  | 0
7 |  | Cable КПСЭнг-FRLS 2х2х0,2 mm2 | m | 15 |  | 0
8 |  | Power cable КВВГнг- LSLTx 4х1,0mm2 | m | 12 |  | 0
9 | 10-01-051-33 | Fastening and connection of cables and conductors: mono pair cable or conductor: high or low frequency on screen | 10 unit | 0.22 |  | 0
10 | 08-02-390-1 | Plastic channels of 40 mm width (mini-channels ТМК1020) | 100 m | 0.22 |  | 0
11 |  | PVC channel (Mini channel ТМК1020) | m | 22 |  | 0
12 | 08-02-406-1 | Metallic constructions (hardware | t | 0.005 |  | 0
|  | Chapter 2. Equipment |  |  |  | 0
13 | Company price | Fire receipt and control equipment with build-in accumulator (EN-54)) "Варта-1/2GSM" | unit | 1 |  | 0
14 | Company price | Intermediate relay 12V, 5А RM -1 | unit | 1 |  | 0
15 | Company price | Fire detector (smoke detector), ИП-8 | unit | 3 |  | 0
16 | Company price | Fire detector (smoke detector), ИП-9 | unit | 3 |  | 0
17 | Company price | Fire detector (manual smoke detector) , ИПР-1 | unit | 2 |  | 0
18 | Company price | Acoustic alarm with intermittent lights, SA-913F | unit | 1 |  | 0
18A | Company price | Motor pump to extinguish the fires with hose length 36 m3/h, including the water hose d=50mm and 60m length (3x20m) and aspiration hose of 6m length | set | 1 |  | 0
19 | Company price | CO2 extinguisher V=5 lit., OY-5CO2 | unit | 4 |  | 0
Total VAT 0 rate | [5 empty] | 0

## FSS
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Installation of biomass heating system and solar hot water production system in the kindergarten of Copceac village, Stefan Voda district
Site: | y
Section: |  | Fuel supply system
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
0
0
Total VAT 0 rate | [5 empty] | 0

## Commiss
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Installation of biomass heating system and solar hot water production system in the kindergarten of Copceac village, Stefan Voda district
Site: | y
Commissioning
No. | Item | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
1 |  | Training of operators | course | 1 |  | 0
2 |  | Measure the emissions | test | 1 |  | 0
3 |  | Measure performance indicators | test | 1 |  | 0
4 |  | Commissioning integral system | system | 1 |  | 0
Total excluding VAT : | [5 empty] | 0
The bidder is responsible for any item that was not attributed a unit price and will be provided without additional costs for the UNDP

## Maintenance
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Installation of biomass heating system and solar hot water production system in the kindergarten of Copceac village, Stefan Voda district
Site: | y
Service and Maintenance works for 3-years of operation
No | Item | Description of item | Periodicity | Quantity for 3 years | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
1 |  | Maintenance works and commissioning of heating system at the beginning of heating season | annual | 3 |  | 0
2 |  | Periodic maintenance works at the end of the heating season | annual | 3 |  | 0
3 |  | Intervention and reparation of equipment in case of emergency | case | 3 |  | 0
4 |  | Telephonic assistance in using the system | permanent | 1 |  | 0
Total excluding VAT : | [5 empty] | 0
* Any equipment or component that requires replacement within the 3 years period and was not included in the list of wear parts shall be treated as a warranty case and must be provided by the contractor at no additional cost

## Boiler
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Installation of biomass heating system and solar hot water production system in the kindergarten of Copceac village, Stefan Voda district
Site: | y
Minimum specifications of boiler
No | Item | Requirements | Suggested requirements | Quantity | Unit price USD | Total, USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | Boiler | Boiler model: |  | 1 | 1 | 1
Fuel type: agro-briquettes, type E, EN 14961-6 (according to Technical Specifications description) *
Limits of emission: EN 303-5:2012 Class 3
Q= 100 kW**
Productivity: minimum 80% ****
Work pressure: ≥1.5 bar
Maximum admitted temperature at operation: ≥85 °C
Power tension: 230V/50Hz
Warranty for active components: 3 years
Warranty for passive components: 5 years
Burner cleaning: automatic cleaning system of burner through mechanical means
Diameter of smoke chimney 200mm***:
Capacity of fuel tank:
Boiler assembling scheme in existing boiler room in accordance with the normative in force *****
Total excluding VAT : | [5 empty] | 1
* Specify type of fuel in accordance with the producer's recommendation
** Based on E type biofuel in accordance with Technical Specifications Description.
*** The bidder may suggest a boiler with higher or lower diameter than specified in project documentation, provided that the smoke chimney is compatible with the boiler and ensures its optimal operation, and the costs are adjusted accordingly in the financial offer.
**** Specify only numerical value. Do not include text
***** The bidder will include an illustration to show the location of boilers in the boiler room by indicating main dimensions