## SITE
REF: | ITB
Lot: | x | Solar panel installation for hot water preparation in the kindergarten of Vadul lui Isac village, Cahul district
Site: | y
Consolidated price list |  |  |  | Estimated amount in USD, 0 rate VAT
Cost Component / Section
1 | Territory development |  |  | 0
2 | Thermomecanics |  |  | 0
3 | Solar hot water preparation system |  |  | 0
4 | Heating and ventilation |  |  | 0
5 | General construction works |  |  | 0
6 | Electricity and lighting |  |  | 0
7 | Automated control and regulation system |  |  | 0
8 | Water and sewage |  |  | 0
9 | Anti fire system |  |  | 0
10 | Fuel system |  |  | 0
11 | Commissioning |  |  | 0
12 | Service and Maintenance works for 3-years of operation |  |  | 0
| Total price of works |  |  | 0
No | Parameter |  | Unit | Value
1 | Annual heat consumption |  | MWh
2 | Boiler efficiency at nominal output |  | percentage | 0%
3 | Annual fuel demand |  | MWh
4 | Net calorific value of the fuel |  | MJ/ton | 15000
5 | Net calorific value of the fuel |  | MWh/ton | 4.1667
6 | Annual fuel consumption |  | ton
7 | Estimated fuel price |  | USD/ton | 110
8 | Annual cost of fuel |  | USD
9 | Discount rate |  | percentage | 10%
10 | Expected lifetime of the boiler |  | years | 10
11 | Current value (VC) of fuel costs |  | USD
Total cost of life-cycle (Price of works + VC fuel) |  |  | USD
Bidder: |  |  | Signature
No changes to the initial structure of this document are allowed. Any modifications made in the document, may result in Bidder's disqualification.

## TA
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solar panel installation for hot water preparation in the kindergarten of Vadul lui Isac village, Cahul district
Site: | y
Section: |  | Territory development
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
0
0
Total VAT 0 rate | [5 empty] | 0

## TM
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solar panel installation for hot water preparation in the kindergarten of Vadul lui Isac village, Cahul district
Site: | y
Section: |  | Thermomecanics
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
0
0
Total VAT 0 rate | [5 empty] | 0

## TMS
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solar panel installation for hot water preparation in the kindergarten of Vadul lui Isac village, Cahul district
Site: | y
Section: |  | Solar hot water preparation system
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Assembling works |  |  |  | 0
1 | IA06M | Heat exchanger with tubes, delivered in 8 sections and mounted in 8 sections (vacuum solar collector APRICUS (30 tubes) or similar) | unit | 6 |  | 0
2 | IA17C | Vertical boiler mounted on floor, boiler having the capacity 1000 l (bivalent heating boiler) | unit | 1 |  | 0
3 | IA38B | Circulating (recirculating) pump mounted on existing pipe, by flanges, with diameter over 2" (GRUNDFOS, SOLAR 25-120 180 or similar) | unit | 1 |  | 0
4 | IA28A | Expending vessel, mounted on platform having the capacity 100 l (expansive membrane tank Varem or similar) | unit | 1 |  | 0
5 | IA17A | Vertical boiler mounted on floor, boiler having the capacity up to 55 l, inclusive (stainless steel drain-back boiler) | unit | 1 |  | 0
6 | IA39A | Installation of water softeners, fully equipped, with water flow 900 -2250 l/h (ANTIKAL, MEDIUM 3/4 or similar) | unit | 2 |  | 0
7 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 20 mm (temperature blending valve) | unit | 1 |  | 0
8 | IA38B | Circulating (recirculating) pump mounted on existing pipe, by flanges, with diameter over 2" ("Biral", Primax15-6 130RED or similar) | unit | 4 |  | 0
|  | Chapter 2. Sanitary works |  |  |  | 0
9 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 20 mm (ball valve with sockets Danfoss) | unit | 5 |  | 0
10 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 25 mm (ball valve with sockets Danfoss) | unit | 15 |  | 0
11 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 25 mm (ball valve with iron grid filter) | unit | 2 |  | 0
12 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 20 mm (safety valve) | unit | 1 |  | 0
13 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 15 mm (safety valve) | unit | 1 |  | 0
14 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 25 mm (brass check valve) | unit | 3 |  | 0
15 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 20 mm (brass check valve) | unit | 3 |  | 0
16 | SE58A | Cold and hot water meters, with diameter -25 mm (single jet water meter) | unit | 1 |  | 0
17 | IC31D | Copper pipe, welded, to connect heating devices and units, in central heating installations, with outer diameter 35,0x1,5 mm (in set with fittings TALOS) | m | 31 |  | 0
18 | IC31C | Copper pipe, welded, to connect heating devices and units, in central heating installations, with outer diameter 22,0x1,0 mm (in set with fittings TALOS) | m | 3 |  | 0
19 | ID06A | Air release valve with mobile tap for central heating systems with nominal diameter 10 mm (аir automatic valve MATIC, "Danfoss") | unit | 4 |  | 0
20 | IC11C | Black steel pipe longitudinally welded, for installations, non-threaded, welded in columns, in central heating installations in residential or social-cultural buildings, pipe with diameter 26,8x2,8 mm (iron-cast) | m | 11 |  | 0
21 | IC11D | Black steel pipe longitudinally welded, for installations, non-threaded, welded in columns, in central heating installations in residential or social-cultural buildings, pipe with diameter 33,5x3,2 mm (iron-cast) | m | 22 |  | 0
22 | RpIF09D | Insulation of pipes with special sleeves for insulation introduced in pipelines, with diameter and thickness from D=35x20 mm (thermal insulated pipe for high temperatures ARMAFLEX) | m | 31 |  | 0
23 | RpIF09D | Insulation of pipes with special sleeves for insulation introduced in pipelines, with diameter and thickness from D=22x20 mm (thermal insulated pipe for high temperatures ARMAFLEX) | m | 3 |  | 0
24 | RpIF09A | Insulation of pipes with special sleeves for insulation introduced in pipelines, with diameter and thickness from D=36x2,5 mm (thermal insulated pipe for high temperatures ARMAFLEX) | m | 22 |  | 0
25 | RpIF09A | Insulation of pipes with special sleeves for insulation introduced in pipelines, with diameter and thickness from D=28x2,5 mm (thermal insulated pipe for high temperatures ARMAFLEX) | m | 11 |  | 0
26 | VA05A | Mounting on site the ventilation ALP tubes , ready-made, with section perimeter 80x2 mm (aluminium frilled tubular box ALUVENT) | m | 4 |  | 0
27 | IC42A | Supports and fasteners for support of pipes, boilers, devices and recipients, having the weight less than 2 kg / unit | kg | 4.85 |  | 0
28 | IzJ09B | Painting tin cover of pipelines and devices with oil pain in 2 layers, including priming | m2 | 1 |  | 0
|  | Chapter 3. Equipment |  |  |  | 0
29 |  | Vacuum solar collector (30 pipes) in set with supports to mount on the roof APRICUS, ETC-30-Fn = 2,83 m2, Q = 2040W or similar | set | 6 |  | 0
30 |  | Mounting support | unit | 6 |  | 0
31 |  | Bivalent heater storage with indirect heat; V = 1000 l, with built-in electronic element 380 V; Nel = 7,5 kW and temperature regulator TESY, EV 15/S2 500 75 F42 or similar | set | 1 |  | 0
32 |  | Pumping block for solar collectors G = 4,6 m3 / h, H =10,5 m, N = 0,11 kW in set with debit meter and thermometer, GRUNDFOS, SOLAR 25-60 130 or similar | set | 1 |  | 0
33 |  | Expending vessel with diaphragm for hot water V = 100 l; P = 6,0 bar Maxivarem LR or similar | set | 1 |  | 0
34 |  | Stainless steel DRAIN BACK boiler, isolated for solar systems V = 55 l; P = 4,0 bar, in set with cooling agent for solar systems, PROGALVA | set | 1 |  | 0
35 |  | Anti-calcar magnetic device DN 20 mm, Q = 2,5 m3 / h, ANTIKAL, MEDIUM 3/4 or similar | set | 2 |  | 0
36 |  | Thermostatic mixing vent DN 20mm, 35-60 ° C, ESBE, VTA 322 35-60 ° C | set | 1 |  | 0
37 |  | Hot water pump G = 1,2 m3 / h, H = 5,1 m, with electrical motor N = 0,003 ... 0,034 kW, EEN <0,15, "Biral", Primax15-6 130RED or similar | unit | 2 |  | 0
38 |  | Hot water recycling pump G = 0,35 m3 / h, H = 6,0m, with electrical motor N = 0,003 ... 0,034 kW, EEN <0,15, "Biral", Primax15-6 130RED or similar | unit | 2 |  | 0
Total VAT 0 rate | [5 empty] | 0

## HV
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solar panel installation for hot water preparation in the kindergarten of Vadul lui Isac village, Cahul district
Site: | y
Section: |  | Heating and ventilation
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
0
0
Total VAT 0 rate | [5 empty] | 0

## GCW
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solar panel installation for hot water preparation in the kindergarten of Vadul lui Isac village, Cahul district
Site: | y
Section: |  | General construction works
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Dismantling |  |  |  | 0
1 | RpCJ35A | Removing internal or external plastering from walls and ceilings | m2 | 38.5 |  | 0
2 | RpCG29C | Demolition of full brick walls, BCA, ceramic blocks or light concrete, GVP bricks, excluding scaffolding and cleaning of bricks | m3 | 0.5 |  | 0
3 | RpCO56A | Dismantling: wood carpentry (doors, windows, blinds, boxes, rolls, masks, etc.) | m2 | 1.7 |  | 0
| RpIzA03A | Prepare plastered or non-plastered concrete or metal surfaces for anticorrosive treatment by cleaning with wire brush | m2 | 4.92 |  | 0
4 | RpCK42C | Dismantling cold floors from concrete, marble, stone, tile, ceramic plates, etc. | m2 | 4.92 |  | 0
5 | RpCU05F | Breaking stone or reinforced concrete walls for pipes or tie rods of 16 -25 cm thickness | unit | 1 |  | 0
6 |  | Rubble |  |  |  | 0
7 | TRI1AA04C3 | Load the materials from group A - light and small by throw - from ramp or ground into vehicle of category 3 | t | 1.2 |  | 0
8 | TsI50A3 | Transport the soil with truck of 5 t to a 3 km distance | t | 1.2 |  | 0
|  | Capitolul 2. Separating walls |  |  |  | 0
9 | CD51C | Brick masonry, format 250 x 120 x 65 on reinforced separating walls with thickness 1/2 brick, height up to 4 m | 100m2 | 0.02 |  | 0
10 |  | Lintel block Т-1 (1 unit) |  |  |  | 0
11 | RpCU06A | Digging trenches 5 cm deep in brick walls of 5 x 50 cm2 | m | 4.1 |  | 0
12 | RpCU02A | Lintels from metallic railways mounted in masonry, including size cut of sleepers | kg | 31.7 |  | 0
13 | CF05A | Internal plastering of 3 cm thickness, executed on wire mesh, plastered with lime cement mortar brand M 100-T for first layer, lime cement mortar brand M 50-T for primer and lime cement mortar brand M 10-T for visible layer, executed manually on flat surfaces, including installing the mesh and fittings on the walls | m2 | 1.1 |  | 0
|  | Capitolul 3. Doors |  |  |  | 0
14 | CK25A | Doors made of plastic profiles including fittings and accessories necessary to doors mounted in masonry of any nature in constructions with height up to 35 m including, in one frame, with surface sheath up to 7 sqm including (PVC, ИД-2) | m2 | 2.54 |  | 0
|  | Capitolul 4. Flooring |  |  |  | 0
15 | CG01A | Support layer for flooring executed from cement mortar M 150-T de 3 cm thickness with finely plastered surface (2 cm thick) | m2 | 3.6 |  | 0
16 | IzF03A1 | Anti-vapour barrier executed on horizontal surfaces with a layer of bitumen cardboard, glued on the entire surface with bitumen membrane | m2 | 3.6 |  | 0
17 | CG01A | Support layer for flooring executed from cement mortar M 150-T de 3 cm thickness with finely plastered surface (2 cm thick) | m2 | 3.6 |  | 0
18 | CG17D1 | Flooring from ceramic tiles including supporting layer of adhesive mortar, executed on surfaces: larger than 16 m2 (13 mm thick) | m2 | 3.6 |  | 0
19 | CI14A | CI14A Linear ceramic tiles applied with adhesive | m | 7.65 |  | 0
|  | Capitolul 5. Interior finishing |  |  |  | 0
20 | CF52B | Interior plastering of 5 mm thickness, manually executed, with dry mixture of plaster, on ceiling, manual preparation of mortar "Knauf" | m2 | 4.92 |  | 0
21 | CN53A | Priming of internal surfaces of walls and ceilings | m2 | 4.92 |  | 0
22 | CN01A | Plain painting with lime, made internally or externally on any support surface with two layers of lime | m2 | 4.92 |  | 0
23 | CF02B | Interior plastering of 2 cm thickness, plastered, manually executed, on walls or pillars, on flat surfaces with lime cement mortar brand M 100-T for spritz, prime and visible layer, on brick walls or small concrete blocks | m2 | 38.5 |  | 0
24 | CF50B | Interior plastering of 5 mm thickness, manually executed, with dry mixture of plaster, on ceiling, manual preparation of mortar "Knauf" | m2 | 38.5 |  | 0
25 | CN53A | Priming of internal surfaces of walls and ceilings | m2 | 38.5 |  | 0
26 | CN06A | Interior painting with co-polymer vinyl in watering emulsion, applied in 2 layers on existing putty, manually executed | m2 | 38.5 |  | 0
|  | Capitolul 6. Foundation FOM 1 (1 unit) |  |  |  | 0
27 | CA03F | Plain concrete poured with classical means, in foundations, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class B12,5 | m3 | 0.16 |  | 0
28 | CL57A | Install and fix the elements into monolith reinforced concrete with weight under 4 kg (МН1) | kg | 4.26 |  | 0
29 | CB02A | Boards from reusable panels, made from resinous short and super short boards to pour the concrete in forms, glass-shaped foundations and platforms for equipment including supports | m2 | 0.55 |  | 0
Total VAT 0 rate | [5 empty] | 0

## EEF
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solar panel installation for hot water preparation in the kindergarten of Vadul lui Isac village, Cahul district
Site: | y
Section: |  | Electricity and lighting
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Assembling works |  |  |  | 0
1 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 1 |  | 0
2 | 08-03-573-4 | Suspended cabinet (panel), height, width and depth, mm, up to (BZUM-TF-100-12) | unit | 1 |  | 0
3 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 2 |  | 0
4 | 08-03-600-2 | Meters mounted on prepared platform, three phases (ZMR110ACe) | unit | 1 |  | 0
5 | 08-03-573-4 | Suspended cabinet (panel), height, width and depth, box for 18 modules КМПн 2/18 IP55, РЩК2 | unit | 1 |  | 0
6 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 11 |  | 0
7 |  | Connecting rail YNS20-3-063 | unit | 2 |  | 0
8 |  | Rail РЕ and N YNN10-14-100 | unit | 4 |  | 0
9 | 08-03-530-4 | General magnetic starter, separated, mounted on wall or column, power up to 40 A ПМА-0247 | unit | 5 |  | 0
10 | 08-03-603-1 | Box with descending transformers ЯТП-0,25-220/12 | unit | 1 |  | 0
11 | 08-03-594-2 | Source of light with luminescent light bulbs mounted separately on pivots, number of light bulbs, in Source of light, 2 ALS.OPL 218 IP54 | 100 unit | 0.01 |  | 0
12 |  | Illuminating devices with fluorescent lights, ceiling ALS.OPL 218 IP54 | unit | 1 |  | 0
13 |  | Torch СГВ-2 | unit | 1 |  | 0
14 |  | Fluorescent lights ЛЛ-18 | unit | 2 |  | 0
15 | 08-03-591-2 | One button switch, open type, hidden Iн=10А, Uн=220В IP43 | 100 unit | 0.01 |  | 0
16 | 08-03-591-8 | Plug socket open type, open switch socket | 100 unit | 0.01 |  | 0
17 | 08-02-472-3 | Earth binding conductor hidden in equalizer layer of floor, flat steel, section 100 mm2 | 100 m | 0.35 |  | 0
18 | 08-02-472-1 | Earth plug, horizontal round steel, diameter 12 mm (round steel D 20mm) | 100 m | 0.8 |  | 0
19 | 08-02-472-1 | Earth plug, horizontal, round steel, diameter 12 mm (round steel D 6mm) | 100 m | 0.5 |  | 0
20 | 08-02-471-4 | Earth plug, vertical, round steel, diameter 20 mm (round steel D=20 mm) | 10 unit | 0.09 |  | 0
21 |  | Thunder collector in set with two clamps | unit | 6 |  | 0
22 | 08-02-146-1 | Cable up to 35 kV, fixed with applied clips, mass 1 m up to: 0,5 kg (ВВГнг(A)-LSLTx-0,66 sec. 3х1,5 mm2) | 100 m | 0.64 |  | 0
23 | 08-02-146-1 | Cable up to 35 kV, fixed with applied clips, mass 1 m up to: 0,5 kg (ВВГнг(A)-LSLTx-0,66 sec. 5х6 mm2) | 100 m | 0.09 |  | 0
24 | 08-02-148-1 | Cable up to 35 kV in posed pipes, blocks, and boxes, mass 1 m up to: 1 kg (ВВГнг(A)-LSLTx-0,66 sec. 5х10 mm2) | 100 m | 0.09 |  | 0
25 | 08-02-146-1 | Cable up to 35 kV, fixed with applied clips, mass 1 m up to: 0,5 kg (ВВГнг(A)-LSLTx-0,66 sec. 5х10 mm2) | 100 m | 0.05 |  | 0
26 | 08-02-146-1 | Cable up to 35 kV, fixed with applied clips, mass 1 m up to: 0,5 kg (ВВГнг(A)-FRLSLTx-0,66 sec. 3x1,5 mm2) | 100 m | 0.04 |  | 0
27 |  | Copper wire cable ВВГнг(A)-LSLTx-0,66 sect. 3х1,5 mm2 | m | 64 |  | 0
28 |  | Copper wire cable ВВГнг(A)-LSLTx-0,66 sect. 5x6 mm2 | m | 9 |  | 0
29 |  | Copper wire cable ВВГнг(A)-LSLTx-0,66 sect. 5x10 mm2 | m | 14 |  | 0
30 |  | Copper wire cable ВВГнг(A)-FRLSLTx-0,66 sect. 3х1,5 mm2 | m | 4 |  | 0
31 | 10-06-034-14 | Different works: cable protection with plastic gutters, on brick or wood walls box 40х20 | m | 9 |  | 0
|  | Chapter 2. Equipment |  |  |  | 0
32 |  | Automatic switch ВА47-29/3/С40 | unit | 1 |  | 0
33 |  | Control panel "BZUM-TF-100-12" | unit | 1 |  | 0
34 |  | Switch ВН 32-3Р/40 | unit | 1 |  | 0
35 |  | Automatic switch ВА47-29/3/С32 | unit | 1 |  | 0
36 |  | Meter 380В, 5-60А, ZMR 110 ACe | unit | 1 |  | 0
37 |  | 18 module box КМПн 2/18 IP55 | unit | 1 |  | 0
38 |  | Power switch ВН-32-3Р-25 | unit | 1 |  | 0
39 |  | Automatic commutator АД14/4/25/30 | unit | 1 |  | 0
40 |  | Automatic switch with one pole ВА47-29/1/C4 | unit | 1 |  | 0
41 |  | Automatic switch with one pole ВА47-29/1/В4 | unit | 1 |  | 0
42 |  | Automatic switch with one pole ВА47-29/1/С2 | unit | 6 |  | 0
43 |  | Automatic switch with one pole ВА47-29/1/В2 | unit | 1 |  | 0
44 |  | Contactor - ПМА-0247 Uн=220В | unit | 5 |  | 0
Total VAT 0 rate | [5 empty] | 0

## ATM
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solar panel installation for hot water preparation in the kindergarten of Vadul lui Isac village, Cahul district
Site: | y
Section: |  | Automated control and regulation system
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Assembling works |  |  |  | 0
1 | 11-02-002-01 | Device installed on flange mix, mass, kg, up to: 1,5 ТНТБ-41, ТПГ100эк | unit | 7 |  | 0
2 | 11-02-001-01 | Device installed on threaded mix, mass, kg, up to: 1,5, (МП4, МВП, ДМ2010) | unit | 11 |  | 0
3 | 11-02-001-01 | Device installed on threaded mix, mass, kg, up to: 1,5 (controller) | unit | 1 |  | 0
4 | 11-03-001-01 | Devices, installed on metallic constructions, panels and console: device, mass, kg, up to: 5 (detector РОС-301) | unit | 1 |  | 0
5 | 11-01-001-01 | Constructions for device installations, mass, kg, up to: 1 (tap) | unit | 19 |  | 0
6 | 08-02-148-1 | Cable up to 35 kV in posed pipes, blocks and boxes, mass 1 m up to: 1 kg | 100 m | 1.65 |  | 0
7 | 08-02-412-9 | Introduce conductors into posed metallic pipes and hoses: each conductor followed by mono or multi wire in joint mesh, summary section up to 6 mm2 ПВ1-0,38 sec.1x1,5 mm2 | 100 m | 0.06 |  | 0
8 | 08-02-411-1 | Metallic hose, outer diameter up to 15 mm (РЗ-ЦХ-Ш15) | 100 m | 0.2 |  | 0
9 | 10-06-034-14 | Various works: cable protection with plastic covers on wood or brick walls | m | 10 |  | 0
10 |  | Warning and control panel ЩУС - box ЯУЭ-1263 dim. 800x600x350 |  |  |  | 0
11 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 34 |  | 0
12 | 11-08-001-04 | Connection of electrical grids to devices by glue | 100 unit. | 0.68 |  | 0
13 |  | Costs of materials |  |  |  | 0
14 |  | Selective device Г-16-225, В-16-225 | unit | 8 |  | 0
15 |  | Selective device Г-16-80, В-16-80 | unit | 11 |  | 0
16 |  | Metallic hose D = 15mm | m | 20 |  | 0
17 |  | Cable channel | m | 10 |  | 0
18 |  | Control cable КВВГнг-LSLTx sect. 4х1,5mm2 | m | 115 |  | 0
19 |  | Control cable КВВГнг-LSLTx sect. 5х1,5mm2 | m | 45 |  | 0
20 |  | Control cable КВВГнг-LSLTx sect. 7х1,5mm2 | m | 5 |  | 0
21 |  | Wire ПВ1-0,38 sect. 1x1,5mm2 | m | 6 |  | 0
|  | Chapter 2 Equipment |  |  |  | 0
22 |  | Thermometer TMTБ41 | unit | 6 |  | 0
23 |  | Thermometer ТПГ100эк-М1 | unit | 1 |  | 0
24 |  | Manometer МП4-У, МВП-Ух0,6 | unit | 9 |  | 0
25 |  | Manometer ДМ2010С | unit | 2 |  | 0
26 |  | Supervisor EUROSTER-813 | unit | 1 |  | 0
27 |  | Sensor relay level РОС-301 | unit | 1 |  | 0
28 |  | Control and warning panel ЩУС-ЯУЭ-1263 800x600x350mm IP54 | unit | 1 |  | 0
29 |  | Relay ПЭ37 | unit | 9 |  | 0
30 |  | Automatic switch ВА47-29/1/С2 | unit | 2 |  | 0
31 |  | Diode D246 | unit | 5 |  | 0
32 |  | Contactor УП5311 | unit | 2 |  | 0
33 |  | Contactor УП5312 | unit | 4 |  | 0
34 |  | Warning devices АD-22DS | unit | 5 |  | 0
35 |  | Button ABLFS-22 | unit | 2 |  | 0
36 |  | Terminal block Бз24-4П | unit | 2 |  | 0
37 |  | Relay РСВ19-11 | unit | 2 |  | 0
38 |  | Chronometer ТЭ | unit | 1 |  | 0
Total VAT 0 rate | [5 empty] | 0

## BK
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solar panel installation for hot water preparation in the kindergarten of Vadul lui Isac village, Cahul district
Site: | y
Section: |  | Water and sewage
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Water pipe |  |  |  | 0
|  | Chapter 1. Sanitary works |  |  |  | 0
1 | SD19A | Straight-way valve with threaded sockets, with diameter 15 mm (stop valve 15кч18р) | unit | 2 |  | 0
2 | SA01A | Galvanized steel pipe for installations, mounted in industrial constructions, with diameter 15 mm | m | 15 |  | 0
3 | SF01A | Tightness test under pressure of hot or cold pipeline executed on steel, zinc pipelines, for installations, longitudinal welded, with diameter 3/8"-2" | m | 15 |  | 0
4 | SF05A | Washing hot or cold water pipelines, executed from steel, zinc pipes, with diameter 3/8"-2" | m | 15 |  | 0
5 | AcE51A | Connect to existing steel pipeline (with nozzle) with nozzle diameter 15 mm | part | 1 |  | 0
|  | Chapter 2. Equipment |  |  |  | 0
6 |  | Extinguisher ОП-5 | unit | 2 |  | 0
|  | Sewage pipeline |  |  |  | 0
7 | SB08C | Pipe from plastic material for sewage, connected with rubber set, mounted apparently or under the flooring, with diameter 50 mm polypropylene | m | 3.3 |  | 0
8 | SF04A | Tightening and functioning test of sewage system made of cast tubes, for drainage, vynil polychrome pipe, non-plasticised, light or from plastic material, ductile iron pipe with diameter up to 100 mm inclusive | 10 m | 0.33 |  | 0
9 | SB08C | Pipe from plastic material for sewage, connected with rubber set, mounted apparently or under the flooring, with diameter 50 mm polypropylene fittings 10% | m | 0.33 |  | 0
10 | AcA25A | Mounting through electric welding of connecting parts, of steel, in position, with diameter 50x100 mm (steel cone) | unit | 2 |  | 0
11 | SB10C | Connecting part (plain ramification) from plastic material for sewage, combined with rubber, with diameter 50 mm (polyethylene review) | unit | 2 |  | 0
12 | SB10C | Connecting part (plain ramification) from plastic material for sewage, combined with rubber, with diameter 50 mm (polyethylene) | unit | 1 |  | 0
Total VAT 0 rate | [5 empty] | 0

## SIP
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solar panel installation for hot water preparation in the kindergarten of Vadul lui Isac village, Cahul district
Site: | y
Section: |  | Anti fire system
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
0
0
Total VAT 0 rate | [5 empty] | 0

## FSS
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solar panel installation for hot water preparation in the kindergarten of Vadul lui Isac village, Cahul district
Site: | y
Section: |  | Fuel system
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
0
0
Total VAT 0 rate | [5 empty] | 0

## Commiss
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solar panel installation for hot water preparation in the kindergarten of Vadul lui Isac village, Cahul district
Site: | y
Commissioning
№ | Item | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
1 |  | Training of operators | course | 1 |  | 0
3 |  | Measure performance indicators | test | 1 |  | 0
4 |  | Commissioning integral system | system | 1 |  | 0
Total excluding VAT: | [5 empty] | 0
The bidder is responsible for any item that was not attributed a unit price and will be provided without additional costs for the UNDP

## Maintenance
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solar panel installation for hot water preparation in the kindergarten of Vadul lui Isac village, Cahul district
Site: | y
Service and Maintenance works for 3-years of operation
No. | Item | Description of item | Periodicity | Quantity for 3 years | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
1 |  | Maintenance works and commissioning | annual | 3 |  | 0
2 |  | Periodic maintenance works at the end of heating season | annual | 3 |  | 0
3 |  | Intervention and repairs in case of emergency | case | 3 |  | 0
4 |  | Telephonic assistance in using the system | permanent | 1 |  | 0
Total excluding VAT : | [5 empty] | 0
* Any equipment or component that requires replacement within the 3 years period and was not included in the list of wear parts shall be treated as a warranty case and must be provided by the contractor at no additional cost

## Boiler
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solar panel installation for hot water preparation in the kindergarten of Vadul lui Isac village, Cahul district
Site: | y
Minimum specifications of boiler
No | Item | Requirements | Suggested requirements | Quantity | Unit price USD | Total, USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | Cazan | Boiler model: |  |  | 1 | 0
Fuel type: agro-briquettes, type E, EN 14961-6 (according to Technical Specifications description) *
Limits of emission: EN 303-5:2012 Class 3
Q= 0 kW**
Productivity: minimum 80% ****
Work pressure: ≥1.5 bar
Maximum admitted temperature at operation: ≥85 °C
Power tension: 230V/50Hz
Warranty for active components: 3 years
Warranty for passive components: 5 years
Burner cleaning: automatic cleaning system of burner through mechanical means
Diameter of smoke chimney ***:
Capacity of fuel tank:
Boiler assembling scheme in existing boiler room in accordance with the normative in force *****
Total excluding VAT : | [5 empty] | 0
* Specify type of fuel in accordance with the producer's recommendation
** Based on E type biofuel in accordance with the Technical Specifications Description.
*** The bidder may suggest a boiler with higher or lower diameter than specified in project documentation, on the condition that the smoke chimney is compatible with the boiler and ensures its optimal operation, and the costs are adjusted accordingly in financial offer.
**** Specify only numerical value. Do not include text
***** The bidder will include an illustration to show the location of boilers in the boiler room by indicating main dimensions