## SITE
REF: | ITB
Lot: | x | Installation of solid biomass heating system and solar panels for hot water production in kindergarten Speranta of Lozova village, Straseni district
Site: | y
Consolidated price list |  |  |  | Estimated amount in USD, 0 rate VAT
Cost Component / Section
1 | Territory development |  |  | 0
2 | Thermomecanics |  |  | 0
3 | Solar hot water production system |  |  | 0
4 | Heating and ventilation |  |  | 0
5 | General construction works |  |  | 0
6 | Electricity and lighting |  |  | 0
7 | Automated control and regulation system |  |  | 0
8 | Water and sewage |  |  | 0
9 | Anti fire system |  |  | 0
10 | Fuel system |  |  | 0
11 | Commissioning |  |  | 0
12 | Service and Maintenance works for 3-years of operation |  |  | 0
| Total price of works |  |  | 0
No | Parameter |  | Unit | Value
1 | Annual heat consumption |  | MWh | 952.12
2 | Boiler efficiency at nominal output |  | percentage | 0%
3 | Annual fuel demand |  | MWh
4 | Net calorific value of the fuel |  | MJ/ton | 15000
5 | Net calorific value of the fuel |  | MWh/ton | 4.1667
6 | Annual fuel consumption |  | ton
7 | Estimated fuel price |  | USD/ton | 110
8 | Annual cost of fuel |  | USD
9 | Discount rate |  | percentage | 10%
10 | Expected lifetime of the boiler |  | years | 10
11 | Current value (VC) of fuel |  | USD
Total cost of life-cycle (Price of works + VC fuel) |  |  | USD
Bidder: |  |  | Signature
No changes to the initial structure of this document are allowed. Any modifications made in the document, may result in Bidder's disqualification.

## TA
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Installation of solid biomass heating system and solar panels for hot water production in kindergarten Speranta of Lozova village, Straseni district
Site: | y
Section: |  | Territory development
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Construction works |  |  |  | 0
|  | Chapter 1.1. Cement-concrete platform |  |  |  | 0
1 | DA06B2 | Layer of cylindrical natural aggregates, having the resistant function of filtering, isolation , ventilation, anti-freeze and proof course, with mechanical laying, with sand | m3 | 5.4 |  | 0
2 | DA06B1 | Layer of cylindrical natural aggregates, having the resistant function of filtering, isolation , ventilation, anti-freeze and proof course, with mechanical laying, with ballast | m3 | 5.4 |  | 0
3 | CG22A | Plain concrete flooring class C 10/8 (Bc 10/B 150) thickness 10 cm, in continuous surface, primed, poured on site, in rooms with surface bigger than 16 sqm (B25 (F200), gr.8 cm) | m2 | 54 |  | 0
4 | DE11A | Small curbs, ready-made from concrete with section 10x15 cm, to delimitate green areas, sidewalks, alleys, etc., placed on concrete foundation B-15, БР 100.20.8 | m | 29 |  | 0
|  | Chapter 1.2. Welded panels (Euro fence) - 25,20 m |  |  |  | 0
5 | CO06B correct | Fencing wire mesh with fence panels made of round steel frame fixed on ready-made reinforced concrete pillars mounted at 2 m distance from each other, interaxed by tamping the ballast, the ridge height of 1,80 m ("GARDLAIN") | m | 25.2 |  | 0
6 | CA03F | Plain concrete poured with classical means in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class В15 | m3 | 0.44 |  | 0
|  | Chapter 1.3. Gate "STANDART" l=1,0m, Н=1,8m (1 unit) |  |  |  | 0
7 | CK14A | Metallic gates with frames made of round steel profiles, ready-made, including the accessories necessary, mounted on reinforced concrete poles, gate STANDART code 6204 | m2 | 1.8 |  | 0
|  | Chapter 1.4. Metallic fence (19,10 m) |  |  |  | 0
8 | TsA02A | Manual digging of soil in limited spaces, under 1,00 m or over 1,00 m in width, executed without support, with vertical slope, in foundations, channels, drainages, twinning steps, in non-cohesive soil or lightly cohesive soil depth < 0,75 m light soil | m3 | 4.2 |  | 0
9 | TsD01B | Scattering with shovel of loose soil, in uniform layers, of 10-30 cm thickness, with a throw of up to 3 m from piles, including smashing the clods, soil from middle ground | m3 | 2.35 |  | 0
10 | TsD04B | Manual punning of piles made in horizontal or inclined digging at 1/4, including watering each soil layer in part with 10 cm thickness of cohesive soil | m3 | 2.35 |  | 0
11 | CO07C correct | Metallic fence of metal and tin frames of 1 mm thickness | kg | 817.76 |  | 0
12 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment | t | 0.82 |  | 0
13 | IzD04A | Painting the articles and metallic constructions with oil paint in 2 layers, executed from profiles, of 8mm-12mm thickness inclusive, with hand brush | t | 0.82 |  | 0
14 | CA03F | Plain concrete poured with classical means in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class В15 | m3 | 2.73 |  | 0
15 | TsC54B | Crushed stone foundation layer | m3 | 0.26 |  | 0
16 | CB02A | Boxes from reusable panels, with boarding from short and super short wood planks to pour the concrete in forms, glass-shaped foundations and equipment platforms including support | m2 | 16.64 |  | 0
|  | Chapter 1.5. Tin gate (1 unit) |  |  |  | 0
17 | CO07C correct | Metallic fence of metal and tin frames of 1 mm thickness | kg | 27.95 |  | 0
18 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment | t | 0.03 |  | 0
19 | IzD04A | Painting the articles and metallic constructions with oil paint in 2 layers, executed from profiles, of 8mm-12mm thickness inclusive, with hand brush | t | 0.03 |  | 0
|  | Chapter 1.7.Steel ash containers Dn0,6х1,0(h) with lid -(6 units) |  |  |  | 0
23 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, all or partially embedded in concrete | kg | 336 |  | 0
24 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment. | t | 0.336 |  | 0
25 | IzD04A | Painting the articles and metallic constructions with oil paint in 2 layers, executed from profiles, of 8mm-12mm thickness inclusive, with hand brush | t | 0.336 |  | 0
|  | Chapter 2. Equipment |  |  |  | 0
26 |  | Wheelbarrow with steel clamp, Vclamp = 0,1m3 | un | 1 |  | 0
|  | Removing fertile soil |  |  |  | 0
27 | TsA02A | Manual digging of soil in limited spaces, under 1,00 m or over 1,00 m in width, executed without support, with vertical slope, in foundations, channels, drainages, twinning steps, in non-cohesive soil or lightly cohesive soil depth < 0,75 m middle ground | m3 | 11 |  | 0
28 | RpCU09A | Manual transportation with wheelbarrow with rubber wheel at 100 m distance, the load of 100 - 120 kg, including setting the circulation cabinets and cleaning the rails of wheelbarrow by loading and unloading through settlement | t | 13.2 |  | 0
|  | Vertical systematization |  |  |  | 0
29 | TsA02B | Manual digging of soil in limited spaces, under 1,00 m or over 1,00 m in width, executed without support, with vertical slope, in foundations, channels, drainages, twinning steps, in non-cohesive soil or lightly cohesive soil depth < 0,75 m middle ground | m3 | 16 |  | 0
30 | RpCU09A | Manual transportation with wheelbarrow with rubber wheel at 100 m distance, the load of 100 - 120 kg, including setting the circulation cabinets and cleaning the rails of wheelbarrow by loading and unloading through settlement | t | 25.6 |  | 0
31 | TsD05B | Mechanical compacting with rammer of 150-200 kg of piles in successive layers of 20-30 cm thickness, excluding watering each layer in part, filling made of cohesive soil | 100 m3 | 0.16 |  | 0
|  | Demolition of buildings and installations |  |  |  | 0
32 | RpCB18F | Demolition of old concrete with mechanical means, plain concrete | m3 | 0.9 |  | 0
33 | TRI1AA04C3 | Loading the materials from group A - light and small by throwing - from a ramp or ground, into vehicles of category 3 | t | 2.16 |  | 0
34 | TsI50A3 | Transportation of soil with truck of 5 t to 3 km distance | t | 2.16 |  | 0
Total VAT 0 rate | [5 empty] | 0

## TM
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Installation of solid biomass heating system and solar panels for hot water production in kindergarten Speranta of Lozova village, Straseni district
Site: | y
Section: |  | Thermomecanics
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Assembling works |  |  |  | 0
1 | IA14D | Monobloc steel heating boiler (hot water 90/70 grades), with caloric power 90 kw and caloric power 225 kW | unit | 2 |  | 0
2 | IA38B | Circulating (recirculating) pump mounted on existing pipe, by flanges, with diameter over 2" | unit | 4 |  | 0
3 | IA28A | Expending vessel, mounted on platform having the capacity V=500 l | unit | 1 |  | 0
4 | IA25A | Pipe sludge separator, in central heating system, with nominal entering diameter 100 mm (dirt trap) | unit | 1 |  | 0
5 | IA38B | Circulating (recirculating) pump mounted on existing pipe, by flanges, with diameter over 2" | unit | 1 |  | 0
6 | IA23A | Liquid fuel filter (Dosaphos 250, Dn20 mm) | unit | 1 |  | 0
7 | IA38B | Circulating (recirculating) pump mounted on existing pipe, by flanges, with diameter over 2" | unit | 2 |  | 0
8 | IA17E | Vertical boiler mounted on floor, boiler having the capacity 4000 l (storage tank for heating system ) | unit | 1 |  | 0
9 | IA25A | Pipe sludge separator, in central heating system, with nominal entering diameter 20 mm (dirt trap) | unit | 2 |  | 0
10 | IA27B | Condenser reservoir, mounted on platform having the capacity 1000 l | unit | 1 |  | 0
11 | IA39A | Installation of water softeners, fully equipped, with water flow 900 -2250 l/h (Decalux-10 ET 500) | unit | 1 |  | 0
12 | ID03B | Three-way plug valve, with flanges with stuffing, for central heating installations, with nominal diameter 50 mm | unit | 1 |  | 0
13 | SE58A | Cold and hot water meters, with diameter -15 mm (caloric energy measuring meter Hydrometer) | unit | 1 |  | 0
|  | Chapter 2. Sanitary works |  |  |  | 0
14 | IzH05B | Pipe insulation with glass wool mattresses, mineral wool type I or type P stitched on one side, on weave of galvanized wire, made on site, having the thickness 60 mm, on pipes with circumference over thermal insulation more than 35 cm (mineral-cotton slabs with synthetic binder brand 75) | m2 | 21.67 |  | 0
15 | IzI09A1 | Protection of thermal insulation of black tin or zinc pipes of 0,5 mm thickness screwed with round slot, self-tapping screws, having the circumference of pipe over thermal insulation between 0,90 and 1,6 m, manufacturing | m2 | 23 |  | 0
16 | IzI09A2 | Protection of thermal insulation of black tin or zinc pipes of 0,5 mm thickness screwed with round slot, self-tapping screws, having the circumference of pipe over thermal insulation between 0,90 and 1,6 m, installation | m2 | 23 |  | 0
17 | IzH40B | Insulation with perforated fiberglass cloth brand "ХПС-Т-5" of pipes of diameter over 25 mm | m2 | 1.212 |  | 0
18 | IzI09A1 | Protection of thermal insulation of black tin or zinc pipes of 0,5 mm thickness screwed with round slot, self-tapping screws, having the circumference of pipe over thermal insulation between 0,90 and 1,6 m, manufacturing | m2 | 39.29 |  | 0
19 | IzI09A2 | Protection of thermal insulation of black tin or zinc pipes of 0,5 mm thickness screwed with round slot, self-tapping screws, having the circumference of pipe over thermal insulation between 0,90 and 1,6 m, installation | m2 | 39.29 |  | 0
20 | IzH05B | Pipe insulation with glass wool mattresses, mineral wool type I or type P stitched on one side, on weave of galvanized wire, made on site, having the thickness 40 mm, on pipes with circumference over thermal insulation more than 35 cm (mineral-cotton mats stitched in metal gauze lining type М2 brand 125) | m2 | 21.93 |  | 0
21 | IzI09A1 | Protection of thermal insulation of black tin or zinc pipes of 0,5 mm thickness screwed with round slot, self-tapping screws, having the circumference of pipe over thermal insulation between 0,90 and 1,6 m, manufacturing | m2 | 24.71 |  | 0
22 | IzI09A2 | Protection of thermal insulation of black tin or zinc pipes of 0,5 mm thickness screwed with round slot, self-tapping screws, having the circumference of pipe over thermal insulation between 0,90 and 1,6 m, installation | m2 | 24.71 |  | 0
23 | CL16B | Thick sheet metal lining (silo funnels, chimney flues, tanks and troughs for sutaje) in chimney flues (chimney flues) | t | 0.479 |  | 0
24 | IA18J | Fine fitting for central heating boilers: faucet control valve (for thermometer ЗКЧ-1-87) | unit | 9 |  | 0
25 | IA18J | Fine fitting for central heating boilers: faucet control valve (for pressure measuring ЗКЧ-275.00.90) | unit | 9 |  | 0
26 | IA18J | Fine fitting for central heating boilers: faucet control valve (for pressure measuring ЗКЧ-287.00.90) | unit | 12 |  | 0
27 | IA18J | Fine fitting for central heating boilers: faucet control valve (for level measuring ЗКЧ-223-89) | unit | 2 |  | 0
28 | ID04F | Stop or retaining valve with jacks for central heating installations, with nominal diameter 100 mm (ball valve JIP Standart FF "Danfoss") | unit | 2 |  | 0
29 | ID04F | Stop or retaining valve with jacks for central heating installations, with nominal diameter 1oo mm (butterfly valve SYLAX (VFY-WH)) | unit | 14 |  | 0
30 | ID04F | Stop or retaining valve with jacks for central heating installations, with nominal diameter 80 mm (butterfly valve SYLAX (VFY-WH)) | unit | 4 |  | 0
31 | ID04B | Stop or retaining valve with jacks for central heating installations, with nominal diameter 40 mm (butterfly valve SYLAX (VFY-WH)) | unit | 4 |  | 0
32 | ID04B | Stop or retaining valve with jacks for central heating installations, with nominal diameter 32 mm (butterfly valve SYLAX (VFY-WH)) | unit | 2 |  | 0
33 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 25 mm (butterfly valve SYLAX (VFY-WH)) | unit | 5 |  | 0
34 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 20 mm (full-opening ball valve UNI ISO 7/1) | unit | 8 |  | 0
35 | ID04F | Stop or retaining valve with jacks for central heating installations, with nominal diameter 100 mm (flange check valve type NVD402 "Danfoss") | unit | 4 |  | 0
36 | ID04B | Stop or retaining valve with jacks for central heating installations, with nominal diameter 40 mm (check valve type NVD402 "Danfoss") | unit | 2 |  | 0
37 | ID04B | Stop or retaining valve with jacks for central heating installations, with nominal diameter 32 mm (check valve type 223 "Danfoss") | unit | 1 |  | 0
38 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 20 mm (check valve type 223 "Danfoss") | unit | 2 |  | 0
39 | ID04C | Stop or retaining valve with jacks for central heating installations, with nominal diameter 50 mm (safety valve 17с29нж) | unit | 1 |  | 0
40 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 25 mm (safety valve 17с29нж) | unit | 4 |  | 0
41 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 15 mm (safety valve 17с29нж) | unit | 2 |  | 0
42 | ID06A | Air release valve with mobile key for central heating installations, with nominal diameter 10 mm (brass automatic air valve with threaded joining type MATIC "Danfoss" VF3, 149 B5 106) | unit | 2 |  | 0
43 | ID06A | Air release valve with mobile key for central heating installations, with nominal diameter 10 mm (two-way safety valve Regulus DBV 1 3/4 Czech Rep) | unit | 2 |  | 0
44 | IC12E | Seamless or longitudinally welded steel pipe for constructions, welded in distribution pipelines, in central heating installations in residential or social-cultural buildings, pipe with outer diameter and wall thickness 108 x 3,5 mm | m | 38 |  | 0
45 | IC12D | Seamless or longitudinally welded steel pipe for constructions, welded in distribution pipelines, in central heating installations in residential or social-cultural buildings, pipe with outer diameter and wall thickness 89 x 3,0 mm | m | 15 |  | 0
46 | IC12A | Seamless or longitudinally welded steel pipe for constructions, welded in distribution pipelines, in central heating installations in residential or social-cultural buildings, pipe with outer diameter and wall thickness 57 x 3,0 mm | m | 20 |  | 0
47 | IC11E | Longitudinally welded black steel pipe for installations, non-threaded, welded in columns, in central heating installations in residential or social-cultural buildings, pipe having the diameter 45 x 2,8 mm | m | 7 |  | 0
48 | IC11D | Longitudinally welded black steel pipe for installations, non-threaded, welded in columns, in central heating installations in residential or social-cultural buildings, pipe having the diameter 38x2,8 mm | m | 6 |  | 0
49 | IC11D | Longitudinally welded black steel pipe for installations, non-threaded, welded in columns, in central heating installations in residential or social-cultural buildings, pipe having the diameter 32x2,8 mm | m | 11 |  | 0
50 | IC11C | Longitudinally welded black steel pipe for installations, non-threaded, welded in columns, in central heating installations in residential or social-cultural buildings, pipe having the diameter 25x2,8 mm | m | 29 |  | 0
51 | IC11B | Longitudinally welded black steel pipe for installations, non-threaded, welded in columns, in central heating installations in residential or social-cultural buildings, pipe having the diameter 20х2,0 mm | m | 1 |  | 0
52 | IE03D | Perform tightness test procedure under pressure of feeding pipelines of heating devices (heaters, thermal convectors, plinth convectors, etc.) with diameter 80 x 3,5 ... 159 x 8 mm | m | 38 |  | 0
53 | IE03C | Perform tightness test procedure under pressure of feeding pipelines of heating devices (heaters, thermal convectors, plinth convectors, etc.) with diameter 54 x 3,5 ... 83 x 3,5 mm | m | 35 |  | 0
54 | IE03B | Perform tightness test procedure under pressure of feeding pipelines of heating devices (heaters, thermal convectors, plinth convectors, etc.) with diameter 1 1/4" ... 2" | m | 24 |  | 0
55 | IE03A | Perform tightness test procedure under pressure of feeding pipelines of heating devices (heaters, thermal convectors, plinth convectors, etc.) with diameter 3/8" ... 1" | m | 30 |  | 0
56 | IE04D | Perform expansion-contraction and running test of pipes in heating installations heaters, thermal convectors, plinth convectors, etc.) with diameter 89 x 3,5 ... 159 x 8 mm | m | 38 |  | 0
57 | IE04C | Perform expansion-contraction and running test of pipes in heating installations heaters, thermal convectors, plinth convectors, etc.) with diameter 54 x 3,5 ... 83 x 3,5 mm | m | 35 |  | 0
58 | IE04B | Perform expansion-contraction and running test of pipes in heating installations heaters, thermal convectors, plinth convectors, etc.) with diameter 1 1/4" ... 2" | m | 24 |  | 0
59 | IE04A | Perform expansion-contraction and running test of pipes in heating installations heaters, thermal convectors, plinth convectors, etc.) with diameter 3/8" ... 1" | m | 30 |  | 0
60 | IC42A | Supports and fasteners for support of pipes, boilers, devices and recipients, having the weight less than 2 kg / unit | kg | 188.31 |  | 0
61 | VA05A | On-site assembling of ALP ventilation tubes, ready-made, having the section perimeter 500 mm (assembling the chimney) | m | 16 |  | 0
62 |  | Metal chimney with dual walls (made from stainless steel - for solid biofuel boilers) inner diameter 500 mm, H = 17,0 m, with thermal insulation - 50 mm, in set: |  |  |  | 0
63 |  | Stainless steel cone-shaped adaptor CF 500/560 | unit | 1 |  | 0
64 |  | Stainless steel wall clip CFO-100 Д560 | unit | 7 |  | 0
65 |  | Stainless steel pipe CF L1000 Д500/560 | unit | 14 |  | 0
66 |  | Stainless steel condensation module CF Д500 | unit | 1 |  | 0
67 |  | Stainless steel lid module CF 87* Д560 | unit | 1 |  | 0
68 |  | Stainless steel tee CF 87* Д500/560 | unit | 1 |  | 0
|  | Chapter 3. Equipment |  |  |  | 0
69 |  | Monobloc steel heating boiler (hot water 90/70 grades), with caloric power 90 kw and 225Kw with solid biofuel burning - pellets, in set with control panel, productivity min 80%, Рnom = 1,5 bar, class 3, ЕН 303-5,2012 | unit | 2 |  | 0
70 |  | Circulating (recirculating) pump mounted on existing pipe, by flanges, with diameter over 2" (outline No.1), productivity Qp=17,2m3/hour, pressure Нр=6,5 m.c.a., N=29 -704 W, class А, А 16-2 (ЕЕ1<0,2) | unit | 2 |  | 0
71 |  | Circulating (recirculating) pump mounted on existing pipe, by flanges, with diameter over 2" (outline No.2), productivity Qp=17,2m3/hour, pressure Нр=21 m.c.a., N=30 -1336 W, class А, А 16-2 (ЕЕ1<0,2 | unit | 2 |  | 0
72 |  | Expending vessel V=500 l, , P=6 bar, 41VE0150 or similar | unit | 1 |  | 0
73 |  | Pipe sludge separator, in central heating system, with nominal entering diameter 100 mm (dirt trap), Р 16 bar, 149В 1802 or similar | unit | 1 |  | 0
74 |  | Circulating (recirculating) pump mounted on existing pipe, by flanges, with diameter over 2" Qp=2,9 m3/hour; Нр-3,5 m.c.a. N=37-96 W, MX 12-2 or similar | unit | 1 |  | 0
75 |  | Proportional water dosing equipment - build-in bypass oxygen D 20 mm, (similar Dosaphos 250) | unit | 1 |  | 0
76 |  | Water circulation pump, mounted on existing pipe, by flanges, with diameter over 2" Qp=0,1 m3/hour, pressure Нр=21,5 m.c.a., N=0,3 кW, BM1-3 or similar | unit | 2 |  | 0
77 |  | Vertical boiler (buffer) for heating system V=4000 L, Р 8 bar | unit | 1 |  | 0
78 |  | Pipe sludge separator, in central heating system, with nominal entering diameter 20 mm (dirt trap), Р 16 bar, 149В 1769 or similar | unit | 2 |  | 0
79 |  | Vessel for additional water, V=1000 L | unit | 1 |  | 0
80 |  | Installation of water softeners, fully equipped, with water flow 900 -2250 l/h (Decalux-5 ET 500 or similar) | unit | 1 |  | 0
81 |  | Universal carrying trolley V=0,1 m3 | unit | 1 |  | 0
82 |  | Three-way plug valve, with flanges with stuffing, for central heating installations, with nominal diameter 50 mm, "Danfoss or similar" | unit | 1 |  | 0
83 |  | Heat meter D 15 mm, "Hydrometer" Sharky 775, h50-15), EN 1434 | unit | 1 |  | 0
Total VAT 0 rate | [5 empty] | 0

## TMS
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Installation of solid biomass heating system and solar panels for hot water production in kindergarten Speranta of Lozova village, Straseni district
Site: | y
Section: |  | Solar hot water production system
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Assembling/installation works |  |  |  | 0
1 | IA06M | Heat exchanger type B - 7 OL, delivered in 8 sections and mounted in 8 sections (vacuum solar collector APRICUS (30 tubes)) | unit | 2 |  | 0
2 | IA17A | Vertical boiler mounted on floor, boiler having the capacity 300 l, inclusive (bivalent heating boiler) | unit | 1 |  | 0
3 | IA38B | Circulating (recirculating) pump mounted on existing pipe, by flanges, with diameter over 2" (GRUNDFOS, SOLAR 25-60 130) | unit | 1 |  | 0
4 | IA28A | Expending vessel, mounted on platform having the capacity 40 l (expansive membrane tank Maxivarem LR) | unit | 1 |  | 0
5 | IA17A | Vertical boiler mounted on floor, boiler having the capacity 20 l, inclusive (stainless steel drain-back boiler) | unit | 1 |  | 0
6 | IA39A | Installation of water softeners, fully equipped, with water flow 900 -2250 l/h (ANTIKAL, MEDIUM 3/4) | unit | 2 |  | 0
7 | ID04A | Three-way plug valve, with flanges with stuffing, for central heating installations, with nominal diameter 20 mm ( temperature blending valve) | unit | 1 |  | 0
8 | IA38B | Circulating (recirculating) pump mounted on existing pipe, by flanges, with diameter over 2" ("Biral", Primax15-6 130RED) | unit | 4 |  | 0
|  | Chapter 2. Sanitary works |  |  |  | 0
9 | ID04A | Three-way plug valve, with flanges with stuffing, for central heating installations, with nominal diameter 15 mm (ball valve with sockets Danfoss) | unit | 7 |  | 0
10 | ID04A | Three-way plug valve, with flanges with stuffing, for central heating installations, with nominal diameter 20 mm (ball valve with sockets Danfoss) | unit | 15 |  | 0
11 | ID04A | Three-way plug valve, with flanges with stuffing, for central heating installations, with nominal diameter 20 mm (ball valve with iron grid filter) | unit | 1 |  | 0
12 | ID04A | Three-way plug valve, with flanges with stuffing, for central heating installations, with nominal diameter 20 mm (safety valve) | unit | 1 |  | 0
13 | ID04A | Three-way plug valve, with flanges with stuffing, for central heating installations, with nominal diameter 15 mm (safety valve) | unit | 1 |  | 0
14 | ID04A | Three-way plug valve, with flanges with stuffing, for central heating installations, with nominal diameter 20 mm (brass check valve) | unit | 5 |  | 0
15 | ID04A | Three-way plug valve, with flanges with stuffing, for central heating installations, with nominal diameter 15 mm (brass check valve) | unit | 2 |  | 0
16 | SE58A | Cold and hot water meters, with diameter -20 mm ( single jet water meter) | unit | 1 |  | 0
17 | IC31C | Copper pipe, welded, to connect heating devices and units, in central heating installations, with outer diameter 22,0x1,0 mm (in set with fittings TALOS) | m | 17 |  | 0
18 | IC11C | Black steel pipe longitudinally welded, for installations, non-threaded, welded in columns, in central heating installations in residential or social-cultural buildings, pipe with diameter 26,8x2,8 mm (iron-cast) | m | 17 |  | 0
19 | IC11B | Black steel pipe longitudinally welded, for installations, non-threaded, welded in columns, in central heating installations in residential or social-cultural buildings, pipe with diameter 21,3x2,8 mm (iron-cast) | m | 8 |  | 0
20 | RpIF09D | Insulation of pipes with special sleeves for insulation introduced in pipelines, with diameter and thickness from D=22x20 mm (thermal insulated pipe for high temperatures ARMAFLEX) | m | 17 |  | 0
21 | VA05A | Mounting on site the ventilation ALP tubes , ready-made, with section perimeter 80x2 mm (aluminium frilled tubular box ALUVENT) | m | 4 |  | 0
22 | IC42A | Supports and fasteners for support of pipes, boilers, devices and recipients, having the weight less than 2 kg / unit | kg | 3.77 |  | 0
23 | IzJ09B | Painting tin cover of pipelines and devices with oil pain in 2 layers, including priming | m2 | 1 |  | 0
|  | Chapter 3. Equipment |  |  |  | 0
24 |  | Vacuum solar collector APRICUS (30 pipes) in set with supports to mount on the roof APRICUS, ETC-30-Fn = 2,83 m2, Q = 2040W | set | 2 |  | 0
25 |  | Mounting support | unit | 2 |  | 0
26 |  | Bivalent heater storage with indirect heat; V = 300 l, in a set with embedded electric element 380 V; Nel = 3,0 kW and temperature regulator TESY, 10 / 7S2 300 | set | 1 |  | 0
27 |  | Pumping block for solar collectors G = 0,90 m3 / h, H = 6,5 m, N = 5,7 m, N = 0,05kW in a set with debit meter and thermometer , GRUNDFOS, SOLAR 25-60 130 or similar | set | 1 |  | 0
28 |  | Expending vessel with diaphragm for hot water V = 40 l; P = 6,0 bar Maxivarem LR or similar | set | 1 |  | 0
29 |  | Izolated stainless steel boiler for solar systems V = 20 l; P = 4,0 bar, in combination with cooling agent for solar systems, PROGALVA or similar | set | 1 |  | 0
30 |  | Anti-calcar magnetic device DN 20 mm, Q = 2,5 m3 / h, ANTIKAL, MEDIUM 3/4 or similar | set | 2 |  | 0
31 |  | Thermostatic mixing vent DN 20mm, 35-60 ° C, ESBE, VTA 322 35-60 ° C or similar | set | 1 |  | 0
32 |  | Hot water pump G = 0,7 m3 / h, H = 5,1m, with electrical motor N = 0,003 ... 0,034kW, EEN <0,15, "Biral", Primax15-6 130RED or similar | unit | 2 |  | 0
33 |  | Recirculation pump of hot water G = 0,1 m3 / h, H = 6,0m, with electrical motor N = 0,003 ... 0,034kW, EEN <0,15, "Biral", Primax15-6 130RED or similar | unit | 2 |  | 0
|  | Control and regulation system |  |  |  | 0
|  | Chapter 1. Assembling works |  |  |  | 0
34 | 11-02-002-01 | Device installed on flange combination, mass, kg, up to: 1,5 ТПГ100эк, ТМТБ | unit | 8 |  | 0
35 | 11-02-001-01 | Device installed on fillet combination, mass, kg, up to: 1,5 (controller) | unit | 1 |  | 0
36 |  | Warning and control panel ЩУС - box ЯУЭ-1263 dim. 1200x600x350 |  |  |  | 0
37 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 4 |  | 0
38 | 11-08-001-04 | Connect the electric grid to devices by glue | 100 unit. | 0.8 |  | 0
39 | 08-02-148-1 | Cable up to 35 kV in pipes, posed blocks and boxes, mass 1 m up to: 1 kg | 100 m | 0.82 |  | 0
40 |  | Cost of materials not included in the price list |  |  |  | 0
41 |  | Selective device Г-16-225, В-16-225 | unit | 4 |  | 0
42 |  | Selective device Г-16-80, В-16-80 | unit | 8 |  | 0
43 |  | Metallic hosepipe D = 15mm | m | 10 |  | 0
44 |  | Control cable КВВГнг-LS sect. 4х1,5mm2 | m | 74 |  | 0
45 |  | Control cable КВВГнг-LS sect. 5х1,5mm2 | m | 8 |  | 0
|  | Chapter 2. Equipment |  |  |  | 0
46 |  | Thermometer ТПГ100эк-М1 | unit | 2 |  | 0
47 |  | Thermometer TMTБ41 | unit | 6 |  | 0
48 |  | Universal commutator УП5311 | unit | 3 |  | 0
49 |  | Chronometer ТЭ | unit | 1 |  | 0
50 |  | Supervisor EUROSTER-813 | unit | 1 |  | 0
|  | Kindergarten. Solar panel for hot water |  |  |  | 0
|  | Chapter 1. Assembling works |  |  |  | 0
51 | IA06M | Heat exchanger type B - 7 OL, delivered in 8 sections and mounted in 8 sections (vacuum solar collector APRICUS (30 tubes)) | unit | 4 |  | 0
52 | IA17B | Vertical boiler mounted on floor, boiler having the capacity 500 l, inclusive (bivalent heating boiler) | unit | 1 |  | 0
53 | IA38B | Circulating (recirculating) pump mounted on existing pipe, by flanges, with diameter over 2" (GRUNDFOS, SOLAR 25-60 130) | unit | 1 |  | 0
54 | IA28A | Expending vessel, mounted on platform having the capacity 60 l (expansive membrane tank Maxivarem LR) | unit | 1 |  | 0
55 | IA17A | Vertical boiler mounted on floor, boiler having the capacity 35 l, inclusive (stainless steel drain-back boiler) | unit | 1 |  | 0
56 | IA39A | Installation of water softeners, fully equipped, with water flow 900 -2250 l/h (ANTIKAL, MEDIUM 3/4) | unit | 2 |  | 0
57 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 20 mm (temperature blending valve) | unit | 1 |  | 0
58 | IA38B | Circulating (recirculating) pump mounted on existing pipe, by flanges, with diameter over 2" ("Biral", Primax15-6 130RED) | unit | 4 |  | 0
|  | Chapter 2. Sanitary works |  |  |  | 0
59 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 15 mm (ball valve with sockets Danfoss) | unit | 5 |  | 0
60 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 20 mm (ball valve with sockets Danfoss) | unit | 15 |  | 0
61 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 20 mm (ball valve with iron grid filter) | unit | 2 |  | 0
62 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 20 mm (safety valve) | unit | 1 |  | 0
63 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 15 mm (safety valve) | unit | 1 |  | 0
64 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 20 mm (brass check valve) | unit | 3 |  | 0
65 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 15 mm (brass check valve) | unit | 3 |  | 0
66 | SE58A | Cold and hot water meters, with diameter -25 mm ( single jet water meter) | unit | 1 |  | 0
67 | IC31D | Copper pipe, welded, to connect heating devices and units, in central heating installations, with outer diameter 28,0x1,5 mm (in set with fittings TALOS) | m | 21 |  | 0
68 | IC31C | Copper pipe, welded, to connect heating devices and units, in central heating installations, with outer diameter 22,0x1,0 mm (in set with fittings TALOS) | m | 2 |  | 0
69 | ID06A | Air release valve with mobile tap for central heating systems, with nominal diameter 10 mm (automatic air valve MATIC, "Danfoss") | unit | 4 |  | 0
70 | IC11B | Black steel pipe longitudinally welded, for installations, non-threaded, welded in columns, in central heating installations in residential or social-cultural buildings, pipe with diameter 21,3x2,8 mm (iron-cast) | m | 11 |  | 0
71 | IC11C | Black steel pipe longitudinally welded, for installations, non-threaded, welded in columns, in central heating installations in residential or social-cultural buildings, pipe with diameter 26,8x2,8 mm (iron-cast) | m | 22 |  | 0
72 | RpIF09D | Insulation of pipes with special sleeves for insulation introduced in pipelines, with diameter and thickness from D=28x20 mm (heat insulating pipe for high temperatures ARMAFLEX) | m | 21 |  | 0
73 | RpIF09D | Insulation of pipes with special sleeves for insulation introduced in pipelines, with diameter and thickness from D=22x20 mm (heat insulating pipe for high temperatures ARMAFLEX) | m | 2 |  | 0
74 | RpIF09A | Insulation of pipes with special sleeves for insulation introduced in pipelines, with diameter and thickness from D=28x2,5 mm (heat insulating pipe for high temperatures ARMAFLEX) | m | 22 |  | 0
75 | RpIF09A | Insulation of pipes with special sleeves for insulation introduced in pipelines, with diameter and thickness from D=22x2,5 mm (heat insulating pipe for high temperatures ARMAFLEX) | m | 11 |  | 0
76 | VA05A | Mounting on site the ventilation ALP tubes , ready-made, with section perimeter 80x2 mm (aluminium frilled tubular box ALUVENT) | m | 4 |  | 0
77 | IC42A | Supports and fasteners for support of pipes, boilers, devices and recipients, having the weight less than 2 kg / unit | kg | 3.77 |  | 0
78 | IzJ09B | Painting tin cover of pipelines and devices with oil pain in 2 layers, including priming | m2 | 1 |  | 0
|  | Chapter 3. Equipment |  |  |  | 0
79 |  | Vacuum solar collector APRICUS (30 pipes) in set with supports to mount on the roof APRICUS, ETC-30-Fn = 2,83 m2, Q = 2040W | set | 4 |  | 0
80 |  | Mounting support | unit | 4 |  | 0
81 |  | Bivalent heater storage with indirect heat; V = 500 l, in set with embedded electric element 380 V; Nel = 7,5 kW and temperature regulator TESY, 10 / 7S2 300 | set | 1 |  | 0
82 |  | Pumping block for solar collectors G =1,6 m3 / h, H = 6,5 m, N = 0,055kW in set with debit meter and thermometer, GRUNDFOS, SOLAR 25-60 130 | set | 1 |  | 0
83 |  | Expending vessel with diaphragm for hot water V = 60 l; P = 6,0 bar Maxivarem LR | set | 1 |  | 0
84 |  | Izolated stainless steel boiler for solar systems V = 35 l; P = 4,0 bar, in combination with cooling agent for solar systems, PROGALVA | set | 1 |  | 0
85 |  | Anti-calcar magnetic device DN 20 mm, Q = 2,5 m3 / h, ANTIKAL, MEDIUM 3/4 | set | 2 |  | 0
86 |  | Thermostatic mixing vent DN 20mm, 35-60 ° C, ESBE, VTA 322 35-60 ° C | set | 1 |  | 0
87 |  | Hot water pump G = 1,2 m3 / h, H = 5,1m, with electric motor N = 0,003 ... 0,034kW, EEN <0,15, "Biral", Primax15-6 130RED | unit | 2 |  | 0
88 |  | Recirculation hot water pump G = 0,35 m3 / h, H = 6,0m, with electric motor N = 0,003 ... 0,034kW, EEN <0,15, "Biral", Primax15-6 130RED | unit | 2 |  | 0
|  | General construction works |  |  |  | 0
|  | Chapter 1. Foundation FOM 1 (1 unit) |  |  |  | 0
89 | RpCK42C | Dismantling cold floors from concrete, marble, stone, tile, ceramic plates, etc. | m2 | 0.73 |  | 0
90 | CA03F | Plain concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class.... (B12,5) | m3 | 0.09 |  | 0
91 | CL57A | Install and fix parts embedded in monolith reinforced concrete with weight under 4 kg (МН1) | kg | 4.26 |  | 0
92 | CB02A | Boxes from reusable panels, with boarding from short and super short wood planks to pour the concrete in forms, glass-shaped foundations and equipment platforms including support | m2 | 0.4 |  | 0
|  | Illumination installations, electric illumination installations |  |  |  | 0
|  | Chapter 1. Assembling works |  |  |  | 0
93 |  | Install the following in existing РЩК1 : |  |  |  | 0
94 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 1 |  | 0
95 | 08-03-573-4 | Suspended cabinet (panel), height, width and depth, mm, up to (BZUM-TF-100-12) | unit | 1 |  | 0
96 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 2 |  | 0
97 | 08-03-600-2 | Meters mounted on prepared platform, three phases (ZMR110ACe) | unit | 1 |  | 0
98 | 08-03-573-4 | Suspended cabinet (panel), height, width and depth, mm, up to, 18 module box КМПн 2/18 IP55, РЩК2 | unit | 1 |  | 0
99 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 10 |  | 0
100 |  | Connecting rail YNS20-3-063 | unit | 2 |  | 0
101 |  | Rail РЕ and N YNN10-14-100 | unit | 4 |  | 0
102 | 08-03-530-4 | General magnetic starter, separated, mounted on wall or column, power up to 40 A ПМА-0247 | unit | 5 |  | 0
103 | 08-03-603-1 | Box with descending transformers ЯТП-0,25-220/12 | unit | 1 |  | 0
104 |  | Torch СГВ-2 | unit | 1 |  | 0
105 | 08-03-591-8 | Plug socket open type, open switch socket | 100 unit | 0.01 |  | 0
106 | 08-02-472-3 | Earth binding conductor hidden in equalizer layer of floor, flat steel, section 100 mm2 | 100 m | 0.2 |  | 0
107 | 08-02-472-1 | Earth plug, horizontal round steel, diameter 12 mm (round steel D 20mm) | 100 m | 0.7 |  | 0
108 | 08-02-472-1 | Earth plug, vertical, round steel, diameter 12 mm (round steel D 6mm) | 100 m | 0.45 |  | 0
109 | 08-02-471-4 | Earth plug, vertical, round steel, diameter 20 mm (round steel D=20 mm) | 10 unit | 0.08 |  | 0
110 |  | Thunder collector in set with two clamps | unit | 4 |  | 0
111 | 08-02-146-1 | Cable up to 35 kV, applied with clamps, mass 1 m up to: 0,5 kg (ВВГнг(A)-LSLTx-0,66 sec. 3х1,5 mm2) | 100 m | 0.47 |  | 0
112 | 08-02-146-1 | Cable up to 35 kV, applied with clamps, mass 1 m up to: 0,5 kg (ВВГнг(A)-LSLTx-0,66 sec. 5х4 mm2) | 100 m | 0.09 |  | 0
113 | 08-02-148-1 | Cable up to 35 kV in posed pipes, blocks and boxes, mass 1 m up to: 1 kg (ВВГнг(A)-LSLTx-0,66 sec. 5х6 mm2) | 100 m | 0.04 |  | 0
114 | 08-02-146-1 | Cable up to 35 kV, applied with clamps, mass 1 m up to: 0,5 kg (ВВГнг(A)-LSLTx-0,66 sec. 5х6 mm2) | 100 m | 0.25 |  | 0
115 | 08-02-146-1 | Cable up to 35 kV, applied with clamps, mass 1 m up to: 0,5 kg (ВВГнг(A)-FRLSLTx-0,66 sec. 3x1,5 mm2) | 100 m | 0.04 |  | 0
116 |  | Cable up to 35 kV, applied with clamps, mass 1 m up to: 0,5 kg (ВВГнг(A)-LSLTx-0,66 sec. 3х1,5 mm2) | m | 47 |  | 0
117 |  | Cable up to 35 kV, applied with clamps, mass 1 m up to: 0,5 kg (ВВГнг(A)-LSLTx-0,66 sec. 5х4 mm2) | m | 9 |  | 0
118 |  | Cable up to 35 kV in posed pipes, blocks and boxes, mass 1 m up to: 1 kg (ВВГнг(A)-LSLTx-0,66 sec. 5х6 mm2) | m | 29 |  | 0
119 |  | Cable up to 35 kV, applied with clamps, mass 1 m up to: 0,5 kg (ВВГнг(A)-FRLSLTx-0,66 sec. 3x1,5 mm2) | m | 4 |  | 0
120 | 10-06-034-14 | Different works: cable protection with plastic gutters, on brick or wood walls box 40х20 | m | 4 |  | 0
|  | Chapter 2. Equipment |  |  |  | 0
121 |  | Automatic switch ВА47-29/3/С32 | unit | 1 |  | 0
122 |  | Control panel "BZUM-TF-100-12" | unit | 1 |  | 0
123 |  | Switch ВН 32-3Р/40 | unit | 1 |  | 0
124 |  | Automatic switch ВА47-29/3/С25 | unit | 1 |  | 0
125 |  | Meter 380В, 5-60А, ZMR 110 ACe | unit | 1 |  | 0
126 |  | 18 module box КМПн 2/18 IP55 | unit | 1 |  | 0
127 |  | Power switch ВН-32-3Р-25 | unit | 1 |  | 0
128 |  | Automatic commutator АД14/4/20/30 | unit | 1 |  | 0
129 |  | Automatic switch with one pole ВА47-29/1/C4 | unit | 1 |  | 0
130 |  | Automatic switch with one pole ВА47-29/1/В4 | unit | 1 |  | 0
131 |  | Automatic switch with one pole ВА47-29/1/С2 | unit | 6 |  | 0
132 |  | Contactor - ПМА-0247 Uн=220В | unit | 5 |  | 0
|  | Control and regulation system |  |  |  | 0
|  | Chapter 1. Assembling works |  |  |  | 0
133 | 11-02-002-01 | Device installed on flange, mass, kg, up to: 1,5 ТНТБ-41, ТПГ100эк | unit | 7 |  | 0
134 | 11-02-001-01 | Device installed on threaded mix, mass, kg, up to: 1,5, (МП4, МВП, ДМ2010) | unit | 11 |  | 0
135 | 11-02-001-01 | Device installed on threaded mix, mass, kg, up to: 1,5 (controller) | unit | 1 |  | 0
136 | 11-03-001-01 | Devices, installed on metallic constructions, panels and console: device, mass, kg, up to: 5 (detector РОС-301) | unit | 1 |  | 0
137 | 11-01-001-01 | Constructions for device installations, mass, kg, up to: 1 (tap) | unit | 19 |  | 0
138 | 08-02-148-1 | Cable up to 35 kV in posed pipes, blocks and boxes, mass 1 m up to: 1 kg | 100 m | 2 |  | 0
139 | 08-02-412-9 | Introduce conductors into posed metallic pipes and hoses: each conductor followed by mono or multi wire in joint mesh, summary section up to 6 mm2 ПВ1-0,38 sec.1x1,5 mm2 | 100 m | 0.06 |  | 0
140 | 08-02-411-1 | Metallic hose, outer diameter up to 15 mm (РЗ-ЦХ-Ш15) | 100 m | 0.2 |  | 0
141 | 10-06-034-14 | Various works: cable protection with plastic covers on wood or brick walls | m | 10 |  | 0
|  | Warning and control panel ЩУС - box ЯУЭ-1263 dim. 800x600x350 |  |  |  | 0
142 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 34 |  | 0
143 | 11-08-001-04 | Connection of electrical grids to devices by glue | 100 units | 0.68 |  | 0
|  | Costs of materials |  |  |  | 0
144 |  | Selective device Г-16-225, В-16-225 | unit | 8 |  | 0
145 |  | Selective device Г-16-80, В-16-80 | unit | 11 |  | 0
146 |  | Metallic hose D = 15mm | m | 20 |  | 0
147 |  | Cable channel | m | 10 |  | 0
148 |  | Control cable КВВГнг-LSLTx sect. 4х1,5mm2 | m | 110 |  | 0
149 |  | Control cable КВВГнг-LSLTx sect. 5х1,5mm2 | m | 85 |  | 0
150 |  | Control cable КВВГнг-LSLTx sect. 7х1,5mm2 | m | 5 |  | 0
151 |  | Wire ПВ1-0,38 sect. 1x1,5mm2 | m | 6 |  | 0
|  | Chapter 2. Equipment |  |  |  | 0
152 |  | Thermometer TMTБ41 | unit | 6 |  | 0
153 |  | Thermometer ТПГ100эк-М1 | unit | 1 |  | 0
154 |  | Manometer МП4-У, МВП-Ух0,6 | unit | 9 |  | 0
155 |  | Manometer ДМ2010С | unit | 2 |  | 0
156 |  | Supervisor EUROSTER-813 | unit | 1 |  | 0
157 |  | Sensor relay level РОС-301 | unit | 1 |  | 0
158 |  | Control and warning panel ЩУС-ЯУЭ-1263 800x600x350mm IP54 | unit | 1 |  | 0
159 |  | Relay ПЭ37 | unit | 9 |  | 0
160 |  | Automatic switch ВА47-29/1/С2 | unit | 2 |  | 0
161 |  | Diode D246 | unit | 5 |  | 0
162 |  | Contactor УП5311 | unit | 2 |  | 0
163 |  | Contactor УП5312 | unit | 4 |  | 0
164 |  | Warning device АD-22DS | unit | 5 |  | 0
165 |  | Button ABLFS-22 | unit | 2 |  | 0
166 |  | Terminal block Бз24-4П | unit | 2 |  | 0
167 |  | Relay РСВ19-11 | unit | 2 |  | 0
168 |  | Chronometer ТЭ | unit | 1 |  | 0
|  | Waterpipe |  |  |  | 0
|  | Chapter 1. Sanitary works |  |  |  | 0
169 | SD19A | Retaining valve with threaded sockets, with diameter15 mm (valve plug 15кч18р) | unit | 2 |  | 0
170 | SA01A | Galvanized steel pipe for installations, mounted in industrial constructions, with diameter 15 mm | m | 6 |  | 0
171 | SF01A | Tightness test under pressure of hot or cold pipeline executed on steel, zinc pipelines, for installations, longitudinally welded, with diameter 3/8"-2" | m | 6 |  | 0
172 | SF05A | Washing hot or cold water pipelines, executed from steel, zinc pipes, with diameter 3/8"-2" | m | 6 |  | 0
173 | AcE51A | Connect to existing steel pipeline (with nozzle) with nozzle diameter 15 mm | part | 1 |  | 0
|  | Chapter 2. equipment |  |  |  | 0
174 |  | Extinguisher ОП-5 | unit | 2 |  | 0
|  | Sewage pipeline |  |  |  | 0
175 | SB08C | Pipe from plastic material for sewage, connected with rubber set, mounted apparently or under the flooring, with diameter 50 mm polypropylene | m | 7 |  | 0
176 | SF04A | Tightening and functioning test of sewage system made of cast tubes, for drainage, vynil polychrome pipe, non-plasticised, light or from plastic material, ductile iron pipe with diameter up to 100 mm inclusive | 10 m | 0.7 |  | 0
177 | SB08C | Pipe from plastic material for sewage, connected with rubber set, mounted apparently or under the flooring, with diameter 50 mm polypropylene fittings 10% | m | 0.7 |  | 0
178 | AcA25A | Mounting through electric welding of connecting parts, of steel, in position, with diameter 50x100 mm (steel cone) | unit | 2 |  | 0
179 | SB10C | Connecting part (plain ramification) from plastic material for sewage, combined with rubber, with diameter 50 mm (polyethylene review) | unit | 2 |  | 0
Total VAT 0 rate | [5 empty] | 0

## HV
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Installation of solid biomass heating system and solar panels for hot water production in kindergarten Speranta of Lozova village, Straseni district
Site: | y
Section: |  | Heating and ventilation
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Heating |  |  |  | 0
1 | IB06A | Steel radiators, monobloc with length up to 1000 mm, inclusive ("Korado" type 33 1000х600(h)) | unit | 2 |  | 0
2 | ID06A | Air release valve with mobile key for central heating installations, with nominal diameter 1/2" (straight locking valve RLV-15) | unit | 2 |  | 0
3 | ID06A | Air release valve with mobile key for central heating installations, with nominal diameter 1/2" (radiator's air release valve) | unit | 4 |  | 0
4 |  | Keys for air inlets R74Y001 | unit | 1 |  | 0
5 | ID06A | Air release valve with mobile key for central heating installations, with nominal diameter 15 mm (automatic air release valve R88IY003 Giacomini) | unit | 2 |  | 0
6 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 15 mm (drainage ball valve Giacomini) | unit | 1 |  | 0
7 | IC13A | Longitudinally welded black steel pipe, for installations, with thread and socket mounted by screwing the connections to devices in central heating installations, pipe with diameter 20x2,0 mm | m | 12 |  | 0
8 | IE03A | Perform tightness test procedure under pressure of feeding pipelines of heating devices (heaters, thermal convectors, plinth convectors, etc.) with diameter 3/8" ... 1" | m | 12 |  | 0
9 | IE04A | Perform thermal expansion and contraction and running test, of feeding pipelines of heating devices (heaters, thermal convectors, plinth convectors, etc.) with diameter 3/8" ... 1" | m | 12 |  | 0
10 | IzJ09B | Painting the tin cover of pipes and devices with 2 layer oil paint, including priming | m2 | 1.56 |  | 0
11 | AcE51A | Connection to existing steel pipeline (with connecting pipes) with the diameter of connecting pipes 15 mm | piesa | 2 |  | 0
|  | Ventilation |  |  |  | 0
12 | VA02A | Manufacturing and mounting of straight ventilation channels, of galvanized steel or aluminium 0,3 - 2 mm thickness, having the perimeter of rectangular section 250 - 700 mm (gr.0,5 mm) | m2 | 4.45 |  | 0
13 | VB28A | Circular deflector with perimeter 900 - 1600 mm, type CR I and CN (D315.00.000) | unit | 1 |  | 0
14 | CC09B | Mounting rabbit mesh to support plaster ceiling , walls, protection of thermal insulators, masking of pipes, applied on straight ceilings, on steel - concrete D = 6-8 mm, with eyelids 26-35 mm inclusive | m2 | 0.2 |  | 0
15 | IzH05B | Insulation of pipes with glass wool mattresses, mineral cotton type I or type P stitched on one side, based on zinc wire, made on site, with thickness 20; 30; 40; 50 or 60 mm, on pipes with circumference over thermal insulation over 30 mm (fiber optic mat, covered with armored aluminium foil gr.50 mm ISOVER-KIM-AL) | m2 | 11 |  | 0
16 |  | Adhesive band for sealing the joints ISOVER AL-TEPPI | m | 20 |  | 0
17 | CL20A | Ventilation grilles ready-made of black sheet, with manually adjustable blinds, painted and embedded in masonry (still air flowing grid SKP 500х500h) | unit | 1 |  | 0
|  | Thermal networks |  |  |  | 0
18 | TsC03B1 | Mechanical digging with excavator of 0,40-0,70 mc, with internal combustion engine and hydraulic control, in ground with natural humidity, unloading in piles ground catg. II | 100 m3 | 0.65 |  | 0
19 | TsA20B | Manual digging of soil, in slopes, in channels cut by excavator or scraper, to fill the digging in slope profile, in middle ground | m3 | 2 |  | 0
20 | TsD02A1 | Scattering loose soil extracted from ground category I or II, by bulldozer tractor on tracks 65-80 CP, in layers of 15-20 cm | 100 m3 | 0.23 |  | 0
21 | TsD05A | Mechanical compacting with rammer of 150-200 kg of piles in successive layers of 20-30 cm thickness, excluding watering each layer in part, filling made of non-cohesive soil | 100 m3 | 0.23 |  | 0
22 | TsD01B | Scattering loose soil with spade, in uniform layers, of 10-30 cm thickness, in one throw up to 3 m from piles, including breaking the clots, soil from middle ground | m3 | 5.8 |  | 0
23 | TsD04B | Manual punning of piles made in horizontal or inclined digging at 1/4, including watering each soil layer in part with 10 cm thickness of cohesive soil | m3 | 5.8 |  | 0
|  | Underground posing |  |  |  | 0
24 | TfA01C2 | Steel pipe mounted in channel at 1-3 m depth or on ground at 3-15m height including cold pressure, tightness test and complex water circulation test with diameter 108x3,5 mm | m | 48 |  | 0
25 | TfA01A2 | Steel pipe mounted in channel at 1-3 m depth or on ground at 3-15m height including cold pressure, tightness test and complex water circulation test with diameter 38х2,0 mm | m | 16 |  | 0
26 | TfA01A2 | Steel pipe mounted in channel at 1-3 m depth or on ground at 3-15m height including cold pressure, tightness test and complex water circulation test with diameter 32х2,0 mm | m | 38 |  | 0
27 | TfA01A2 | Steel pipe mounted in channel at 1-3 m depth or on ground at 3-15m height including cold pressure, tightness test and complex water circulation test with diameter 45х2,0 mm | m | 30 |  | 0
28 | TfA02C2 | Ready-made steel elbow or corner, mounted on pipe embedded in channel, at 1-3 m depth or on ground at 3-15m height including cold pressure, tightness test and complex water circulation test with diameter 108 mm (pipe bend) | unit | 6 |  | 0
29 | TfB02E2 | Mounting slide valve, with vent or stop valve made of steel or iron-cast up to Pn 40, in channel at 1-3 m depth or on ground up to 3-15 m with nominal diameter Dn 100 mm (ball valve LD-WW) | unit | 2 |  | 0
30 | TfB02A2 | Mounting slide valve, with vent or stop valve made of steel or iron-cast up to Pn 40, in channel at 1-3 m depth or on ground up to 3-15 m with nominal diameter Dn 40 mm (ball valve LD-WW) | unit | 4 |  | 0
31 | TfB02A2 | Mounting slide valve, with vent or stop valve made of steel or iron-cast up to Pn 40, in channel at 1-3 m depth or on ground up to 3-15 m with nominal diameter Dn 32 mm (ball valve LD-WW) | unit | 1 |  | 0
32 | TfB02A2 | Mounting slide valve, with vent or stop valve made of steel or iron-cast up to Pn 40, in channel at 1-3 m depth or on ground up to 3-15 m with nominal diameter Dn 25 mm (ball valve LD-WW) | unit | 5 |  | 0
33 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, all or partially embedded in concrete | kg | 85.47 |  | 0
|  | Channel КЛ-90х45-8 (15 m) |  |  |  | 0
34 | CA02C | Plain concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class B12,5 | m3 | 2.04 |  | 0
35 | CP16A | Mount L- and U-type elements, pre-cast from reinforced steel for channels (thermal, heating, cables, etc.) hod Л6-8 | unit | 5 |  | 0
36 | CP16B | Mount pre-cast elements from reinforced steel for channels (thermal, heating, cables, etc.), straight or curved plates П8-8 | unit | 5 |  | 0
37 | CP10B | Mount pre-cast elements from reinforced steel in residential and social-cultural buildings with monolith reinforced concrete structure, mixt or bearing masonry, at height up to 20 m including with volume from 0,2-2,5 mc bearing block ОП-1 | unit | 16 |  | 0
38 | CP10B | Mount pre-cast elements from reinforced steel in residential and social-cultural buildings with monolith reinforced concrete structure, mixt or bearing masonry, at height up to 20 m including with volume from 0,2-2,5 mc bearing block ОП-2 | unit | 16 |  | 0
|  | Channel КЛ-120х45-8 (6 m) |  |  |  | 0
39 | CA02C | Plain concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class B12,5 | m3 | 1.01 |  | 0
40 | CP16A | Mount L- and U-type elements, pre-cast from reinforced steel for channels (thermal, heating, cables, etc.) hod Л10-8 | unit | 2 |  | 0
41 | CP16B | Mount pre-cast elements from reinforced steel for channels (thermal, heating, cables, etc.), straight or curved plates П11-8 | unit | 2 |  | 0
|  | Channel КЛ-60х45-8 (6 m) |  |  |  | 0
42 | CA02C | Plain concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class B12,5 | m3 | 0.59 |  | 0
43 | CP16A | Mount L- and U-type elements, pre-cast from reinforced steel for channels (thermal, heating, cables, etc.) hod Л6-8 | unit | 2 |  | 0
44 | CP16B | Mount pre-cast elements from reinforced steel for channels (thermal, heating, cables, etc.), straight or curved plates П8-8 | unit | 2 |  | 0
|  | Pipe nozzle УТ 1 |  |  |  | 0
|  | Thermal chamber 1,8х2,4х2,0(h) |  |  |  | 0
45 | CP50A | Install ready-made concrete elements. Block-wall for basement, weight 0,5 t. Note: type of ready-made element is included accord. to project FC-5м | unit | 4 |  | 0
46 | CP50A | Install ready-made concrete elements. Block-wall for basement, weight 0,5 t. Note: type of ready-made element is included accord. to project FC-5-8м | unit | 12 |  | 0
47 | CP50A | Install ready-made concrete elements. Block-wall for basement, weight 0,5 t.Note: type of ready-made element is included accord. to project ФБС12.5.3-Т | unit | 6 |  | 0
48 | CP16B | Mount pre-cast elements from reinforced steel for channels (thermal, heating, cables, etc.), straight or curved plates ПO-4 | unit | 2 |  | 0
49 | CA03G | Reinforced concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, reinforced concrete class... В15, ФМ-2в | m3 | 2.38 |  | 0
50 | CC01F | Concrete steel fittings OB 37 prepared in site workshop and mounted with bar diameter more than 8 mm including in continuous foundations and radiation | kg | 176.7 |  | 0
51 | CA03F | Plain concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class.... B7,5 | m3 | 1.94 |  | 0
52 | CB02A | Boards from reusable panels, made from resinous short and super short boards to pour the concrete in forms, glass-shaped foundations and platforms for equipment including supports | m2 | 9.5 |  | 0
53 | AcE07A | Install steel or concrete steel lids on manholes of water and sewage systems, offroad type I Т | unit | 2 |  | 0
54 | CP16B | Mount pre-cast elements from reinforced steel for channels (thermal, heating, cables, etc.), straight or curved plates КЦО-1 | unit | 2 |  | 0
55 | CL10C | Metallic stairs, landings, bridges, bars and constructions to support technological equipment or metallic platforms for large aggregates delivered in ready-made sub-sets , at height up to 35 m, with weight up to 0,150 t, welded | t | 0.05 |  | 0
56 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment. | t | 0.05 |  | 0
57 | IzD04A | Painting metallic articles and constructions with oil paint in 2 layers, executed in profiles, with thickness between 8mm and 12mm inclusive, with hand brush | t | 0.05 |  | 0
58 | CA03G | Reinforced concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, reinforced concrete class... B7,5, drainage system and DP-1 | m3 | 2.8 |  | 0
|  | Drainage pit ДК1 |  |  |  | 0
59 | AcE14A | Executing the manholes from ready-made reinforced concrete elements, for sewage, circular (ring) with diameter 1,5 m, in soil without underground water | m3 | 1.99 |  | 0
60 | AcE14A1 | Ready-made reinforced concrete elements of manholes,circular (ring) with diameter 1,5 m, in soil without underground water. Note: resource with 0,00 (zero) norm is in accordance with the project | unit | 1 |  | 0
61 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment. | t | 0.03 |  | 0
62 | IzD04A | Painting metallic articles and constructions with oil paint in 2 layers, executed in profiles, with thickness between 8mm and 12mm inclusive, with hand brush | t | 0.03 |  | 0
63 | CA02C | Plain concrete poured in equalizer, slopes height up to 35 m inclusive, prepared with concrete mixer acc. art. CA01 or commercial concrete, poured with classical means B7,5 | m3 | 0.57 |  | 0
64 | CA03F | Plain concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class.... B7,5 | m3 | 0.4 |  | 0
65 | DB16A | Asphalt concrete coat with small aggregates, executed at warm temperatures, in thickness of 2,5 cm manual laying | m2 | 4.2 |  | 0
66 | AcA16B | Install asbestos cement tubes assembled with steel sockets with flanges with the length 3 m and diameter 150 mm | m | 3 |  | 0
67 | TfB01H1 | Mounting slide valve, with vent or stop valve made of steel or iron-cast up to Pn 25, in channel at 1m depth or on ground up to 3 m with nominal diameter Dn 150 mm (automatic safety valve) | unit | 1 |  | 0
|  | Mine ШО1, ШО2 (2 units) |  |  |  | 0
68 | CA03F | Plain concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class.... B15 | m3 | 2.84 |  | 0
69 | CA03F | Plain concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class.... B7,5 | m3 | 0.4 |  | 0
70 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, all or partially embedded in concrete | kg | 50.12 |  | 0
71 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, all or partially embedded in concrete | kg | 160 |  | 0
72 | DB16A | Asphalt concrete coat with small aggregates, executed at warm temperatures, in thickness of 2,5 cm manual laying | m2 | 4.2 |  | 0
73 | IzF04F | Hydro-insulated layer executed at warm temperature on terraces, roofs, or foundations on soils without underground waters, including mouldings of current hydro-insulation on inclined up to 40% or vertical, plane or curved surfaces, with bitumen or rubber bitumen applied with brush or rubber pump (purlin) lacquer БТ-577 | m2 | 4.2 |  | 0
74 | CC02E | Concrete steel fittings OB 37 prepared in site workshop, with bar diameter up to 8 mm inclusive, for plates, excluding constructions executed with sliding plates | kg | 11.9 |  | 0
75 | CC02F | Concrete steel fittings OB 37 prepared in site workshop, with bar diameter over 8 mm, for plates, excluding constructions executed with sliding plates | kg | 21.12 |  | 0
|  | Mine ШО3 (1 unit) |  |  |  | 0
76 | CA03F | Plain concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class.... М300 | m3 | 1.3 |  | 0
77 | CA03F | Plain concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class.... B7,5 | m3 | 0.3 |  | 0
78 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, all or partially embedded in concrete | kg | 19.69 |  | 0
79 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, all or partially embedded in concrete | kg | 59.6 |  | 0
80 | DB16A | Asphalt concrete coat with small aggregates, executed at warm temperatures, in thickness of 2,5 cm manual laying | m2 | 1.52 |  | 0
81 | IzF04F | Hydro-insulated layer executed at temperature on terraces, roofs, or foundations on soils without underground waters, including mouldings of current hydro-insulation on inclined up to 40% or vertical, plane or curved surfaces, with bitumen or rubber bitumen applied with brush or rubber pump (purlin) lacquer БТ-577 | m2 | 1.52 |  | 0
82 | CC02E | Concrete steel fittings OB 37 prepared in site workshop, with bar diameter up to 8 mm inclusive, for plates, excluding constructions executed with sliding plates | kg | 11.9 |  | 0
83 | CC02F | Concrete steel fittings OB 37 prepared in site workshop, with bar diameter over 8 mm, for plates, excluding constructions executed with sliding plates | kg | 21.12 |  | 0
|  | Nozzle "А" (4 units) |  |  |  | 0
84 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, all or partially embedded in concrete | kg | 4.8 |  | 0
85 | CE05A | Covers from anticorrosive profiled tin, curled or wrinkled, fixed with clamps, executed with dual stitches, executed on surfaces wider than 40 sqm from profiled tin sheets of 0.4mm thickness, including execution of aprons, connection to chimneys etc. | m2 | 2.36 |  | 0
86 | IzF04F | Hydro-insulated layer executed at warm temperature on terraces, roofs, or foundations on soils without underground waters, including mouldings of current hydro-insulation on inclined up to 40% or vertical, plane or curved surfaces, with bitumen or rubber bitumen applied with brush or rubber pump (purlin) lacquer БТ-577 | m2 | 0.68 |  | 0
87 | IzH05B | Pipe insulation with glass wool mattresses, mineral wool type I or type P stitched on one side, on weave of galvanized wire, made on site, having the thickness 60 mm, on pipes with circumference over thermal insulation over 35 cm (mineral-cotton mats stitched on synthetic binder type 125, 50 mm thick | m2 | 24 |  | 0
88 | IzH40B | Insulation with perforated fiberglass cloth brand "ХПС-Т-5" of pipes of diameter over 25 mm | m3 | 0.61 |  | 0
89 | IzI05B | Thermo-insulation protection of pipes, executed with bitumen wire mesh type I A, tied with soft steel wire with diameter 1,25 mm РСТ | m2 | 55.1 |  | 0
90 | IzF04F k=2 | Hydro-insulated layer executed at warm temperature on terraces, roofs, or foundations on soils without underground waters, including mouldings of current hydro-insulation on inclined up to 40% or vertical, plane or curved surfaces, with bitumen or rubber bitumen applied with brush or rubber pump (purlin) 2 layers od cold bithumen | m2 | 45 |  | 0
91 |  | Dismantling and redo the asphaltic concrete |  |  |  | 0
92 | DG05A k=3 | Dismantle the coat up to 3 cm thickness, formed of permanent asphaltic coats, alphaltic concrete | m2 | 8 |  | 0
93 | DG01A | Breaking sidewalks or foundations made of stones, clocks or gravel or stones set on sand | m2 | 8 |  | 0
94 | TsC54A | Sand foundation layer | m3 | 1.2 |  | 0
95 | TsC54B | Stone foudnation layer | m3 | 1.2 |  | 0
96 | DB16D k=2,5 | Asphalt concrete coat with small aggregates, executed at hot temperatures, in thickness of 4 cm manual laying (10 cm thick) | m2 | 8 |  | 0
|  | Aerial mounting and entry nozzle |  |  |  | 0
97 | TfA01C1 | Steel pipe mounted in channel at up to 1 m depth or on ground at 3m height including cold pressure, tightness test and complex water circulation test with diameter 108x3,5 mm | m | 48 |  | 0
98 | TfA01A1 | Steel pipe mounted in channel at up to 1 m depth or on ground at 3m height including cold pressure, tightness test and complex water circulation test with diameter 57x3,0 mm | m | 4 |  | 0
99 | TfA01A1 | Steel pipe mounted in channel at up to 1 m depth or on ground at 3m height including cold pressure, tightness test and complex water circulation test with diameter 38x2,0 mm | m | 10 |  | 0
100 | TfA01A1 | Steel pipe mounted in channel at up to 1 m depth or on ground at 3m height including cold pressure, tightness test and complex water circulation test with diameter 32x2,0 mm | m | 10 |  | 0
101 | TfA02C1 | Ready-made steel elbow or cross-over installed on pipe amplasata in channel, at up to 1 m depth or on ground at 3m height including cold pressure, tightness test and complex water circulation test with diameter 108 mm (pipe bend) | unit | 6 |  | 0
102 | TfA02C1 | Ready-made steel elbow or cross-over installed on pipe amplasata in canal, at up to 1 m depth or on ground at 3m height including cold pressure, tightness test and complex water circulation test with diameter 100х50 mm (reducing pipe) | unit | 2 |  | 0
103 | TfB02E1 | Mounting slide valve, with vent or stop valve made of steel or iron-cast up to Pn 40, in channel at 1m depth or on ground up to 3 m with nominal diameter Dn 100 mm (ball valve LD-WW) | unit | 2 |  | 0
104 | TfB02B1 | Mounting slide valve, with vent or stop valve made of steel or iron-cast up to Pn 40, in channel at 1m depth or on ground up to 3 m with nominal diameter Dn 50 mm (ball valve LD-WW) | unit | 4 |  | 0
105 | TfB02A1 | Mounting slide valve, with vent or stop valve made of steel or iron-cast up to Pn 40, in channel at 1m depth or on ground up to 3 m with nominal diameter Dn 20 mm (ball valve LD-WW)) | unit | 2 |  | 0
106 | AcE51C | Connection to existing steel pipeline (with connecting pipes) with the diameter of connecting pipes 100 mm | piesa | 2 |  | 0
107 | AcE51A | Connection to existing steel pipeline (with connecting pipes) with the diameter of connecting pipes 50 mm | piesa | 2 |  | 0
108 | IC44C | Manufacture, mounting and installation of safety pipe through masonry, pipe having the diameter 159 x 4 mm (L=0,5m) | unit | 2 |  | 0
109 | IC44A | Manufacture, mounting and installation of safety pipe through masonry, pipe having the diameter 57х3,0 mm (L=0,5 m) | unit | 2 |  | 0
110 | IC42A | Supports and fasteners for support of pipes, boilers, devices and recipients, having the weight less than 2 kg / unit | kg | 30 |  | 0
111 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, all or partially embedded in concrete | kg | 0.04 |  | 0
112 | IzH05B | Pipe insulation with glass wool mattresses, mineral wool type I or type P stitched on one side, on weave of galvanized wire, made on site, having the thickness 60 mm, on pipes with circumference over thermal insulation over 35 cm (mineral-cotton slabs with synthetic binder brand 125 thick50mm) | m2 | 24 |  | 0
113 | IzH40B | Insulation with perforated fiberglass cloth brand "ХПС-Т-5" of pipes of diameter over 25 mm | m3 | 1.2 |  | 0
114 | IzI09A1 | Protection of thermal insulation of black tin or zinc pipes of 0,5 mm thickness screwed with round slot, self-tapping screws, having the circumference of pipe over thermal insulation between 0,90 and 1,6 m, assembled | m2 | 33.3 |  | 0
115 | IzI09A2 | Protection of thermal insulation of black tin or zinc pipes of 0,5 mm thickness screwed with round slot, self-tapping screws, having the circumference of pipe over thermal insulation between 0,90 and 1,6 m, manufacturing | m2 | 33.3 |  | 0
116 | IzJ09B | Painting tin cover of pipelines and devices with oil pain in 2 layers, including priming | m2 | 14 |  | 0
|  | Supports ОП1 (ОП2) |  |  |  | 0
117 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, all or partially embedded in concrete | kg | 16.6 |  | 0
118 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment. | t | 0.02 |  | 0
119 | IzD04A | Painting metallic articles and constructions with oil paint in 2 layers, executed in profiles, with thickness between 8mm and 12mm inclusive, with hand brush | t | 0.02 |  | 0
120 | CA03F | Plain concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class.... B15 | m3 | 0.25 |  | 0
121 | GA08A | Steel pipe protection tube mounted in trench when crossing the roads to protect the pipeline, the tube with diameter T Dn 50 mm | m | 5 |  | 0
|  | Coating the channel |  |  |  | 0
|  | Lateral |  |  |  | 0
122 | CD50A | Plain brick masonry, format 250 x 120 x 65 for outer walls with height up to 4 m | m3 | 3.63 |  | 0
123 | IzF23A | Protection layer on thermal insulation over cellular polystyrene plates with bitumen cardboard or glass bitumen wire mesh glued with bitumen type H 68/75 on polystyrene plates, including gluing the margins of cardboard or mesh when assembling | m2 | 30.24 |  | 0
124 |  | Covering plates |  |  |  | 0
125 | CG01A | Support flooring layer executed from cement mortar M 100-T of 3 cm thickness with finely plastered surface | m2 | 30.96 |  | 0
126 | IzF23A | Protection layer on thermal insulation over cellular polystyrene plates with bitumen cardboard or glass bitumen wire mesh glued with bitumen type H 68/75 on polystyrene plates, including gluing the margins of cardboard or mesh when assembling | m2 | 30.96 |  | 0
127 | CG01A | Support flooring layer executed from cement mortar M 100-T of 3 cm thickness with finely plastered surface (gr.2 cm) | m2 | 30.96 |  | 0
|  | Lower side of channels |  |  |  | 0
128 | CG01A | Support flooring layer executed from cement mortar M 100-T of 3 cm thickness with finely plastered surface (gr.2 cm) | m2 | 26.52 |  | 0
129 | IzF23A | Protection layer on thermal insulation over cellular polystyrene plates with bitumen cardboard or glass bitumen wire mesh glued with bitumen type H 68/75 on polystyrene plates, including gluing the margins of cardboard or mesh when assembling | m2 | 26.52 |  | 0
130 | CG01A | Support flooring layer executed from cement mortar M 100-T of 3 cm thickness with finely plastered surface (gr.2 cm) | m2 | 26.52 |  | 0
|  | Hydro insulation of drainage pit DK1 |  |  |  | 0
131 | 41-01-001-1 | Insulation with plastering on horizontal surfaces made of concrete with asphalt poured in two layers : 10 mm each | 100m2 | 0.03 |  | 0
132 | IzF04F k=2 | Hydro-insulated layer executed at warm temperature on terraces, roofs, or foundations on soils without underground waters, including mouldings of current hydro-insulation on inclined up to 40% or vertical, plane or curved surfaces, with bitumen or rubber bitumen applied with brush or rubber pump (purlin) (2 layers) | m2 | 12.72 |  | 0
Total VAT 0 rate | [5 empty] | 0

## GCW
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Installation of solid biomass heating system and solar panels for hot water production in kindergarten Speranta of Lozova village, Straseni district
Site: | y
Section: |  | General construction works
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Ground works |  |  |  | 0
1 | TsC03B1 | Mechanical digging with excavator of 0,40-0,70 mc, with internal combustion engine and hydraulic control, in soil with natural humidity, unloaded in piles on ground catg. II | 100 m3 | 0.33 |  | 0
2 | TsA20B | Manual digging of soil, in slopes, in channels cut by excavator or scraper, to fill the digging in slope profile, in middle ground | m3 | 1.02 |  | 0
3 | TsD02A1 | Scattering loose soil extracted from ground category I or II, by bulldozer tractor on tracks 65-80 CP, in layers of 15-20 cm | 100 m3 | 0.13 |  | 0
4 | TsD01B | Scattering loose soil with spade, in uniform layers of 10-30 cm thickness, in a 3 m throw from pile, including breaking the clods, soil from middle ground | m3 | 3.27 |  | 0
5 | TsD04B | Manual punning of piles executed in horizontal or inclined digging at 1/4, including watering each layer of ground in part, having 10 cm thickness cohesive soil | m3 | 16.36 |  | 0
|  | Chapter 2. Foundation |  |  |  | 0
6 | TsC54B | Crushed stone foundation layer | m3 | 1.73 |  | 0
7 | CA03F | Plain concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class.... (B12,5) | m3 | 18.1 |  | 0
8 | CB02A | Boards from reusable panels, made from resinous short and super short boards to pour the concrete in forms, glass-shaped foundations and platforms for equipment including supports | m2 | 90.45 |  | 0
9 | IzF50A | Hydro insulation made from liquid glass cement mortar in foundations and walls applied on horizontal surfaces | m2 | 11.52 |  | 0
|  | Chapter 3. Wall |  |  |  | 0
10 | CD50A | Plain brick masonry, format 250 x 120 x 65 for outer walls with height up to 4 m | m3 | 40.1 |  | 0
11 | CC03A | Mounting welded meshes at height less or equal to 35 m, on walls and diaphragms, with weight of mesh up to 3 kg/mp СГ-1 | kg | 66.4 |  | 0
12 | IC44C | Manufacture, mounting and installation of safety pipe through masonry, pipe having the diameter 159 x 2,8 mm (L=0,45 m) | unit | 2 |  | 0
13 | IC44E | Manufacture, mounting and installation of safety pipe through masonry, pipe having the diameter 325 x 4 mm (L=0,45 m) | unit | 2 |  | 0
14 | IC44B | Manufacture, mounting and installation of safety pipe through masonry, pipe having the diameter 108x2,8 mm (L=0,45 m) | unit | 2 |  | 0
15 |  | Lintels Прм 1, Прм 2 |  |  |  | 0
16 | CA04F | Concrete poured in slabs, beams, pillars, prepared by concrete mixer or commercial concrete according to art. CA01 and pouring with classical means В15 | m3 | 0.48 |  | 0
17 | CC02K | Concrete steel fittings OB 37 prepared in site workshop, with bar diameter up to 8 mm including, and mounted in beams and pillars, at height less or equal to 35 m, excluding constructions executed with sliding plates | kg | 11.4 |  | 0
18 | CC02L | Concrete steel fittings OB 37 prepared in site workshop, with bar diameter more than 8 mm, mounted in beams and pillars, at height less or equal to 35 m, excluding constructions executed with sliding plates | kg | 22 |  | 0
19 | CB02D | Boards from reusable panels, made from resinous short and super short boards to pour concrete in pillars and frames excluding supports at height up to 20 m including | m2 | 4.3 |  | 0
|  | Chapter 4. Overlapping |  |  |  | 0
20 | CP53B | Floor tiles and cover for constructions, in areas with earthquakes 7-8 with support on 2 sides at the height of the building up to 35 m, with surface up to 10 m2 Note: type of ready-made element will be included according to project (1ПК53-12-4,5-С7) | unit | 4 |  | 0
21 | CP53B | Floor tiles and cover for constructions, in areas with earthquakes 7-8 with support on 2 sides at the height of the building up to 35 m, with surface up to 10 m2 Note: type of ready-made element will be included according to project (1ПК53-12-4,5-С7) | unit | 3 |  | 0
22 |  | Monolith reinforced concrete belt Пм1 |  |  |  | 0
23 | CA04F | Concrete poured in slabs, beams, pillars, prepared by concrete mixer or commercial concrete according to art. CA01 and pouring with classical means В15 | m3 | 2.3 |  | 0
24 | CC02K | Concrete steel fittings OB 37 prepared in site workshop, with bar diameter up to 8 mm including, and mounted in beams and pillars, at height less or equal to 35 m, excluding constructions executed with sliding plates | kg | 34.2 |  | 0
25 | CC02L | Concrete steel fittings OB 37 prepared in site workshop, with bar diameter more than 8 mm, mounted in beams and pillars, at height less or equal to 35 m, excluding constructions executed with sliding plates | kg | 196.6 |  | 0
26 | CB02C | Boards from reusable panels, made from resinous short and super short boards to pour concrete in plates and beams excluding supports at height up to 20 m inclusive | m2 | 13.25 |  | 0
27 | RpCU05F | Breaking stone or reinforced concrete walls of 16 -25 cm thickness to embed pipes | unit | 1 |  | 0
|  | Chapter 5.Roof |  |  |  | 0
28 | RpCU06C | Dig trenches of up to 5 cm depth in stone or reinforced concrete walls of 5 x 50 cm2 | m | 1.2 |  | 0
29 | CA04F | Concrete poured in slabs, beams, pillars, prepared by concrete mixer or commercial concrete according to art. CA01 and pouring with classical means В12,5 | m3 | 0.1 |  | 0
30 | CB02C | Boards from reusable panels, made from resinous short and super short boards to pour concrete in plates and beams excluding supports at height up to 20 m inclusive | m2 | 0.96 |  | 0
31 | CL57A | Mounting and fixing the embedded parts in monolith reinforced concrete: weight less than 4 kg | kg | 3.18 |  | 0
32 | CE17A | Additional ondutiss polymer layer mounted under the tile layer, corrugated or indented tiles (vapour barrier sheet) | m2 | 45.25 |  | 0
33 | IzF10F | Thermal insulation layer on terraces, roofs and flooring, made of mineral cotton type G 80 or G 100, made of mineral cotton type PIB, glued with bitumen on horizontal or inclined surfaces up to 40 % (mineral cotton Y=125 kg/m3, gr.150 mm) | m2 | 45.25 |  | 0
34 | CE17A | Additional ondutiss polymer layer mounted under the tile layer, corrugated or indented tiles (hydro insulation sheet) | m2 | 45.25 |  | 0
35 | IzF18B k=2 | Support layer of equalizer or protection for insulation, including related mouldings, executed with ready-made cement mortar brand M50-T without lime, plastered, on horizontal or inclined surfaces up to 40 % inclusive, applied in average thickness of 2 cm (gr.4 cm) | m2 | 45.25 |  | 0
36 | CE41A | Mounting rafters with antiseptic treatment | m3 | 1.55 |  | 0
| CN50A | Fire-proofing of carpentry; Fire-proofing of carpentry farms, acres, beams, rafters, wall plates | m3 | 1.55 |  | 0
37 | CE17A | Additional ondutiss polymer layer mounted under the tile layer, corrugated or indented tiles ( anti-condensation sheet) | m2 | 73 |  | 0
38 | CE30B | Roof covering or tile covering, eternal type plates etc., from unprocessed resinous boards (24 mm thickness) sanded on one side, in ordinary constructions | m2 | 81 |  | 0
39 | CN51F | Antiseptic treatment of carpentry, on apparent surfaces with antiseptic: beams, wall plates. | 100m2 | 0.44 |  | 0
40 | CN50C | Fire-proofing of carpentry; mesh for covering and flooring. | 100m2 | 0.44 |  | 0
41 | CE40A | Mounting elements of beam frame (bars) with antiseptic treatment | m3 | 0.1 |  | 0
42 | CN50A | Fire-proofing of carpentry; Fire-proofing of carpentry farms, ackres, beams, rafters, wall plates | m3 | 0.1 |  | 0
43 | CE31C | Clogged gutter, with apparent corbel, from soft resinous boards and sanded on one side, with average width 0,4 m | m2 | 20 |  | 0
44 | CN50A | Fire-proofing of carpentry; Fire-proofing of carpentry farms, acres, beams, rafters, wall plates | m3 | 0.45 |  | 0
45 | CN51B | Antiseptic treatment of carpentry, on hidden surfaces with antiseptic: timber frame. | m3 | 0.45 |  | 0
46 | CN16D | Painting with lacquers and oil paint applied on wood carpentry, executed in 2 layers of enamel paint on floors | m2 | 20 |  | 0
47 | CE06A | Covers from anticorrosive profiled tin, curled or wrinkled, mounted on metallic panels, executed on surfaces wider than 40 mp from profiled tin sheets connected with special clips or mechanical screws, of superior flange, including execution of aprons, connection to chimneys etc. (profiled sheet "LIDER" ЛК-20) | m2 | 81 |  | 0
48 | CE20A | Gutter systems brass type of anticorrosive protected tin Dn100 mm | m | 18.8 |  | 0
49 | CE22A | Pipe systems brass type of anticorrosive protected tin Dn100 mm | m | 16.5 |  | 0
50 | CE05B | Covers from anticorrosive zinc or plane sheet, fixed with clips, executed in double nots in both directions, executed on surfaces wider than 40 mp with tin sheets of 0,5 mm thickness, including execution of aprons, connection to chimneys etc. (painted sheet "LIDER") | m2 | 20 |  | 0
51 | CK28B | Suspended ceilings executed on site of PFL or melamine PAL with plastic profiles (veneer) | m2 | 24 |  | 0
52 | IC43C | Manufacture, mounting and installation of safety pipe through panels, pipe having the diameter 133 x 3 mm (L=0,32 m) | unit | 1 |  | 0
53 | IC43E | Manufacture, mounting and installation of safety pipe through panels, pipe having the diameter 355 x 4 mm (L=0,32 m) | unit | 1 |  | 0
54 | CL20A | Ready-made black tin ventilation grilles, with manually adjustable blinds, painted and mounted in masonry ( louvered grille Жр-1, 780x580) | unit | 1 |  | 0
55 |  | Canopy К-1 |  |  |  | 0
56 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, fully or partially embedded in concrete | kg | 25.44 |  | 0
57 | IzD05A | Manual priming with one layer of lead paint of technological equipment | t | 0.03 |  | 0
58 | IzD04A | Painting metallic articles and constructions with oil paint in 2 layers, executed from profiles with thickness between 8mm and 12mm including, with hand brush | t | 0.03 |  | 0
59 | CL57A | Mounting and fixing the embedded parts in monolith reinforced concrete: weight less than 4 kg | kg | 8.84 |  | 0
60 | CE06A | Covers from anticorrosive profiled tin, curled or wrinkled, mounted on metallic panels, executed on surfaces wider than 40 mp from profiled tin sheets connected with special clips or mechanical screws, of superior flange, including execution of aprons, connection to chimneys, etc. (profiled sheet "LIDER" ЛК-20) | m2 | 2.8 |  | 0
61 | CE05B | Covers from anticorrosive zinc or plane sheet, fixed with clips, executed in double nots in both directions, executed on surfaces wider than 40 mp with tin sheets of 0,5 mm thickness, including execution of aprons, connection to chimneys, etc. (gr.0,8 mm) | m2 | 0.7 |  | 0
62 | CA05E | Concrete poured in straight walls, diaphragms, and different special constructions, situated above zero rate, at height up to 35 m including, prepared by concrete mixer or commercial concrete according to art.CA01 and pouring with classical means, reinforced concrete class... В15 | m3 | 0.14 |  | 0
|  | Chapter 6. Windows and doors |  |  |  | 0
63 | CK57C | Mounting PVC profiles: tilted (inclined, swing-out) with gap surface under 2 m2 in one frame | m2 | 3.91 |  | 0
64 | CK12A | Metallic doors made from laminated steel profile, steel profiles prepared at cold temperatures, including fittings and accessories necessary to doors mounted in masonry of any nature in constructions with height up to 35 m inclusive, in one frame, with surface sheath up to 7 mp including (ИД-1) | m2 | 2.1 |  | 0
65 | CN20B | Internal or external painting on metallic carpentry with alkyd enamel in 2 layers including priming | m2 | 4.62 |  | 0
66 | CK25A | Doors made of plastic profiles including fittings and accessories necessary to doors mounted in masonry of any nature in constructions with height up to 35 m including, in one frame, with surface sheath up to 7 mp including (PVC, ИД-2) | m2 | 0.92 |  | 0
|  | Chapter 7. Flooring |  |  |  | 0
67 | TsC53B | Compacting the ground with crushed stone | 100m2 | 0.45 |  | 0
68 | CG22A | Flooring from plain concrete class C 10/8 (Bc 7,5/B 100) in thickness of 10 cm, in continuous surface, plastered, poured on site, in rooms with surface larger than 16 sqm (gr.8 cm) | m2 | 45.24 |  | 0
69 | CC03C | Mounting welded meshes at height less or equal to 35 m, plates (5 BpI- 100x100) | kg | 83.7 |  | 0
70 | IzF03A1 | Anti-vapour barrier executed on horizontal surfaces with a layer of bitumen cardboard, glued on the entire surface with bitumen membrane | m2 | 45.24 |  | 0
71 | CG01A | Support layer for flooring executed from cement mortar M 150-T de 3 cm thickness with finely plastered surface (gr.2 cm) | m2 | 45.24 |  | 0
72 | CG17D | Flooring from ceramic tiles including supporting layer of adhesive mortar, executed on surfaces: larger than 16 m2 (gr.13 mm) | m2 | 45.24 |  | 0
73 | CI14A | Linear ceramic tiles applied with adhesive | m | 26.25 |  | 0
|  | Chapter 8. Interior finishing |  |  |  | 0
74 | CF52B | Interior plastering of 5 mm thickness, manually executed, with dry mixture of plaster, on ceiling, manual preparation of mortar "Knauf" | m2 | 45.24 |  | 0
75 | CN53A | Priming of internal surfaces of walls and ceilings | m2 | 45.24 |  | 0
76 | CN01A | Plain painting with lime, made internally or externally on any support surface with two layers of lime | m2 | 45.24 |  | 0
77 | CF02B | Interior plastering of 2 cm thickness, plastered, manually executed, on walls or pillars, on flat surfaces with lime cement mortar brand M 100-T for spritz, prime and visible layer, on brick walls or small concrete blocks | m2 | 92.32 |  | 0
78 | CN53A | Priming of internal surfaces of walls and ceilings | m2 | 92.32 |  | 0
79 | CN06A | Interior painting with co-polymer vinyl in watering emulsion, applied in 2 layers on existing putty, manually executed | m2 | 92.32 |  | 0
|  | Chapter 9. External finishing |  |  |  | 0
81 | CF11A | External plastering sprayed on brick or concrete walls (with brush or pump) of 3 cm thickness, manually executed, with lime cement mortar M 50-T for spritz and lime cement mortar M 25-T for prime and visible layer in continuous surface | m2 | 6.35 |  | 0
|  | Chapter 10. Other works |  |  |  | 0
|  | Chapter 10.1. External stairs and ramp |  |  |  | 0
82 | TsA02B | Manual digging of soil in limited spaces, under 1,00 m or over 1,00 m in width, executed without support, with vertical slope, in foundations, channels, drainages, twinning steps, in non-cohesive soil or lightly cohesive soil depth < 0,75 m light soil | m3 | 1.65 |  | 0
83 | TsD01B | Scattering loose soil with spade, in uniform layers of 10-30 cm thickness, in a 3 m throw from pile, including breaking the clods, soil from middle ground | m3 | 0.85 |  | 0
84 | TsD04B | Manual punning of piles executed in horizontal or inclined digging at 1/4, including watering each layer of ground in part, having 10 cm thickness cohesive soil | m3 | 0.85 |  | 0
85 | TsC54B | Crushed stone foundation layer | m3 | 0.2 |  | 0
86 | CA03F | Plain concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class.... B7,5 | m3 | 1.4 |  | 0
87 | CB02A | Boards from reusable panels, made from resinous short and super short boards to pour the concrete in forms, glass-shaped foundations and platforms for equipment including supports | m2 | 7.4 |  | 0
88 | CG22A1 | Flooring from plain concrete class C 10/8 (Bc 7,5/B 100) in thickness de 10 cm, in continuous surface, plastered, poured on site, in rooms with surface smaller or equal to 16 sqm (В15, gr.2 cm) | m2 | 3.4 |  | 0
|  | Chapter 10.2. Fom 1 ... Fom 5 |  |  |  | 0
89 | TsC54B | Crushed stone foundation layer | m3 | 1.28 |  | 0
90 | CA03G | Reinforced concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, reinforced concrete class... В15 | m3 | 2.38 |  | 0
91 | CA03G | Reinforced concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, reinforced concrete class... В12,5 | m3 | 0.48 |  | 0
92 | CA03F | Plain concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class.... B12,5 | m3 | 0.26 |  | 0
93 | CC01C | Concrete steel fittings OB 37 prepared in site workshop and mounted with bar diameter up to 8 mm including in isolated foundations | kg | 15.92 |  | 0
94 | CC01D | Concrete steel fittings OB 37 prepared in site workshop and mounted with bar diameter more than 8 mm including in isolated foundations | kg | 68.8 |  | 0
95 | CL57A | Mounting and fixing the embedded parts in monolith reinforced concrete: weight less than 4 kg | kg | 69.08 |  | 0
96 | CB02A | Boards from reusable panels, made from resinous short and super short boards to pour the concrete in forms, glass-shaped foundations and platforms for equipment including supports | m2 | 10 |  | 0
|  | Chapter 10.3. Support ОП2 (2 units), ОП3 (4 units) |  |  |  | 0
97 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, fully or partially embedded in concrete | kg | 18.92 |  | 0
98 | IzD05A | Manual priming with one layer of lead paint of technological equipment | t | 0.02 |  | 0
99 | IzD04A | Painting metallic articles and constructions with oil paint in 2 layers, executed from profiles with thickness between 8mm and 12mm including, with hand brush | t | 0.02 |  | 0
100 | CA05E | Reinforced concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, reinforced concrete class... В12,5 | m3 | 0.06 |  | 0
|  | Chapter 10.4. Support ОП4 (9 units) |  |  |  | 0
101 | CL57A | Mounting and fixing the embedded parts in monolith reinforced concrete: weight less than 4 kg | kg | 18.27 |  | 0
102 | IzD05A | Manual priming with one layer of lead paint of technological equipment | t | 0.02 |  | 0
103 | IzD04A | Painting metallic articles and constructions with oil paint in 2 layers, executed from profiles with thickness between 8mm and 12mm including, with hand brush | t | 0.02 |  | 0
|  | Chapter 10.5. Support ОП5 (1 unit) |  |  |  | 0
104 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, fully or partially embedded in concrete | kg | 6.25 |  | 0
105 | IzD05A | Manual priming with one layer of lead paint of technological equipment | t | 0.01 |  | 0
106 | IzD04A | Painting metallic articles and constructions with oil paint in 2 layers, executed from profiles with thickness between 8mm and 12mm including, with hand brush | t | 0.01 |  | 0
|  | Chapter 10.7. Metallic platform ПМ1 (1 unit) |  |  |  | 0
110 | CL10C | Metallic stairs, landings, bridges, bars and constructions to support technological equipment or metallic platforms for large aggregates delivered in ready-made sub-sets , at height up to 35 m, with weight up to 0,150 t, welded | t | 0.26 |  | 0
111 | IzD05A | Manual priming with one layer of lead paint of technological equipment | t | 0.26 |  | 0
112 | IzD04A | Painting metallic articles and constructions with oil paint in 3 layers, executed from profiles with thickness between 8mm and 12mm including, with hand brush | t | 0.26 |  | 0
|  | Chapter 10.8. Chimney flue |  |  |  | 0
113 | TsA02B | Manual digging of soil in limited spaces, having under 1,00 m or over 1,00 m width, executed without support, with vertical slope, in foundations, channels, basements, twinning steps, in non-cohesive soil or slightly cohesive soil at the depth < 0,75 m middle ground | m3 | 10.35 |  | 0
114 | TsD01B | Scattering loose soil with spade, in uniform layers of 10-30 cm thickness, in a 3 m throw from pile, including breaking the clods, soil from middle ground | m3 | 5.3 |  | 0
115 | TsD04B | Manual punning of piles executed in horizontal or inclined digging at 1/4, including watering each layer of ground in part, having 10 cm thickness cohesive soil | m3 | 5.3 |  | 0
116 | CA02C | Plain concrete poured in equalizers, slopes at height up to 35 m including, prepared by concrete mixer according to art. CA01 or commercial concrete, poured with classical means B3,5 | m3 | 0.73 |  | 0
117 | CA03G | Reinforced concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, reinforced concrete class... В12,5 | m3 | 6.3 |  | 0
118 | CC01C | Concrete steel fittings OB 37 prepared in site workshop and mounted with bar diameter up to 8 mm including in isolated foundations | kg | 5.2 |  | 0
119 | CC01D | Concrete steel fittings OB 37 prepared in site workshop and mounted with bar diameter more than 8 mm including in isolated foundations | kg | 223.8 |  | 0
120 | CB02A | Boards from reusable panels, made from resinous short and super short boards to pour the concrete in forms, glass-shaped foundations and platforms for equipment including supports | m2 | 15.3 |  | 0
121 | CG01A | Support layer for flooring executed from cement mortar M 150-T of 3 cm thickness with finely plastered surface (gr.5 cm) | m2 | 2.25 |  | 0
122 | CG01A1 k=4 | Support layer for flooring executed from cement mortar M 150-T of 3 cm thickness with finely plastered surface. The difference for each 0.5 cm of support layer of mortar M 150-T, should be added or deducted | m2 | 2.25 |  | 0
123 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, fully or partially embedded in concrete | tn | 1.72 |  | 0
124 | IzD05A | Manual priming with one layer of lead paint of technological equipment | t | 1.72 |  | 0
125 | IzD04A k=1.5 | Painting metallic articles and constructions with oil paint in 3 layers, executed from profiles with thickness between 8mm and 12mm including, with hand brush | t | 1.72 |  | 0
|  | Chapter 10.9. Drywall |  |  |  | 0
126 | TsC54B | Crushed stone foundation layer | m3 | 3.75 |  | 0
127 | CA02C | Plain concrete poured in equalizers, slopes at height up to 35 m inclusive, prepared by concrete mixer according to art. CA01 or commercial concrete, poured with classical means B12,5 | m3 | 2.63 |  | 0
Total VAT 0 rate | [5 empty] | 0

## EEF
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Installation of solid biomass heating system and solar panels for hot water production in kindergarten Speranta of Lozova village, Straseni district
Site: | y
Section: |  | Electricity and lighting
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Assembling works |  |  |  | 0
1 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 1 |  | 0
2 | 08-03-573-4 | Suspended cabinet (panel), height, width and depth, mm, up to (BZUM-TF-100-12) | unit | 1 |  | 0
3 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 2 |  | 0
4 | 08-03-600-2 | Meters mounted on prepared platform, with three phases (ZMR110ACe) | unit | 1 |  | 0
5 | 08-03-573-4 | Suspended cabinet (panel), height, width and depth, box for 24 modules КМПн 2/24 IP55 | unit | 1 |  | 0
6 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 3 |  | 0
7 |  | Connecting rail YNS20-3-063 | unit | 2 |  | 0
8 |  | Rail РЕ and N YNN10-14-100 | unit | 4 |  | 0
9 | 08-03-573-4 | Suspended cabinet (panel), height, width and depth, box for 24 modules КМПн 2/24 IP55 | unit | 1 |  | 0
10 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 20 |  | 0
11 |  | Connecting rail YNS20-3-063 | unit | 2 |  | 0
12 |  | Rail РЕ and N YNN10-14-100 | unit | 4 |  | 0
13 | 08-03-573-4 | Suspended cabinet (panel), height, width and depth, (extensive box К654У2) | unit | 1 |  | 0
14 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 1 |  | 0
15 |  | Plug socket with grounding contact IP54 | unit | 1 |  | 0
16 |  | Flexible cable КГ (А) LS 3х10 mm2 | m | 10 |  | 0
17 | 08-03-530-4 | General magnetic starter, separated, mounted on wall or column, power up to 40 A ПМА-0247 | unit | 13 |  | 0
18 | 08-03-603-1 | Box with descending transformers ЯТП-0,25-220/12 | unit | 1 |  | 0
19 | 08-03-594-2 | Source of light with luminescent light bulbs mounted separately on pivots, number of light bulbs, in Source of light, 2 ALS.OPL 218 IP54 | 100 unit | 0.04 |  | 0
20 | 08-03-594-2 | Source of light with luminescent light bulbs mounted separately on pivots, number of light bulbs, in Source of light, 2 СД 218 | 100 unit | 0.01 |  | 0
21 |  | Illuminating devices with fluorescent lights, ceiling ALS.OPL 218 IP54 | unit | 4 |  | 0
22 |  | Illuminating devices with compact fluorescent lights, ceiling CD 218 IP54 | unit | 1 |  | 0
23 |  | Torch СГВ-2 | unit | 1 |  | 0
24 |  | luminescent light bulbs ЛЛ-18 | unit | 8 |  | 0
25 |  | Compact luminescent light bulbs ЛЛК-18 | unit | 2 |  | 0
26 | 08-03-591-2 | One button switch, open type, hidden Iн=10А, Uн=220В IP43 | 100 unit | 0.02 |  | 0
27 | 08-03-591-8 | Plug socket open type, open switch socket | 100 unit | 0.02 |  | 0
28 | 08-02-472-3 | Eath binding conductor hidden in equalizer layer of floor, flat steel, section 100 mm2 | 100 m | 0.3 |  | 0
29 | 08-02-471-4 | Earth plug, vertical, round steel, diameter 20 mm (round steel D=20 mm) | 10 unit | 0.06 |  | 0
30 | 08-02-472-1 | Earth binding conductor: earth plug, horisontal, made of round steel, diameter 12 mm | 100 m | 0.54 |  | 0
31 | 08-02-146-1 | Cable up to 35 kV, fixed with applied clips, mass 1 m up to: 0,5 kg (ВВГнг(А)-LS-066 sec. 3х1,5 mm2) | 100 m | 2.1 |  | 0
32 | 08-02-148-1 | Cable up to 35 kV posed in pipes, blocks and boxes, mass 1 m up to: 1 kg (ВВГнг(А)-LS-066 sec. 3х1,5 mm2) | 100 m | 0.15 |  | 0
33 | 08-02-146-1 | Cable up to 35 kV, fixed with applied clips, mass 1 m up to: 0,5 kg (ВВГнг(А)-LS-066 sec. 4х2,5 mm2) | 100 m | 0.22 |  | 0
34 | 08-02-146-1 | Cable up to 35 kV fixed with applied clips, mass 1 m up to: 0,5 kg (ВВГнг(А)-LS-066 sec. 5х2,5 mm2) | 100 m | 0.05 |  | 0
35 | 08-02-148-1 | Cable up to 35 kV posed in pipes, blocks and boxes, mass 1 m up to: 1 kg (ВВГнг(А)-LS-066 sec. 5х6 mm2) | 100 m | 0.02 |  | 0
36 | 08-02-146-1 | Cable up to 35 kV fixed with applied clips, mass 1 m up to: 0,5 kg (ВВГнг(A)-LS-066 sec. 5х10 mm2) | 100 m | 0.05 |  | 0
37 | 08-02-146-1 | Cable up to 35 kV, fixed with applied clips, mass 1 m up to: 0,5 kg (ВВГнг(А)-FRLS-066 sec. 3х1,5 mm2) | 100 m | 0.07 |  | 0
38 |  | Copper wire cable ВВГнг(A)-LS-066 sect. 3x1,5 mm2) | m | 225 |  | 0
39 |  | Copper wire cable ВВГнг(A)-LS-066 sect. 4х2,5 mm2 | m | 22 |  | 0
40 |  | Copper wire cable ВВГнг(A)-LS-0,66 sect. 5х2,5 mm2 | m | 5 |  | 0
41 |  | Copper wire cable ВВГнг(A)-LS-0,66 sect. 5х6,0 mm2 | m | 8 |  | 0
42 |  | Copper wire cable ВВГнг(A)-LS-0,66 sect. 5х10,0 mm2 | m | 5 |  | 0
43 |  | Copper wire cable ВВГнг(A)-FRLS-0,66 sect. 3х1,5 mm2 | m | 7 |  | 0
44 | 08-02-407-6 | Steel pipe on constructions installed in primed channels executed, on flooring support, diameter up to 20 mm (steel pipe) | 100 m | 0.13 |  | 0
45 | 08-02-411-1 | Metallic hose, outer diameter up to 15 mm (metallic sleeve РЗ-ЦХ-Д20 mm) | 100 m | 0.13 |  | 0
46 | 10-06-034-14 | Different works: cable protection with plastic gutters, on brick or wood walls box 40х20 | m | 0.05 |  | 0
|  | Chapter 2. Equipment |  |  |  | 0
47 |  | Automatic switch ВА47-29/3/С40 | unit | 1 |  | 0
48 |  | Control panel "BZUM-TF-100-12" | unit | 1 |  | 0
49 |  | Switch ВН 32-3Р/40 | unit | 1 |  | 0
50 |  | Automatic switch ВА47-29/3/С32 | unit | 1 |  | 0
51 |  | Active electrical energy meter ZMR110ACe, Iн=5-60А, U=380V | unit | 1 |  | 0
52 |  | 24-module box КМПн 2/24 IP55 | unit | 1 |  | 0
54 |  | Switch ВН 32-3Р/32 | unit | 1 |  | 0
55 |  | Automatic switch ВА47-29/3/С25 | unit | 1 |  | 0
56 |  | Box to install 24 modules КМПн 2/24 IP55 | unit | 1 |  | 0
57 |  | Switch ПП-3P-25 | unit | 1 |  | 0
58 |  | Automatic switch АД14/4/16/30 | unit | 1 |  | 0
59 |  | Three-way automatic switch ВА47-29/3/С10 | unit | 2 |  | 0
60 |  | Three-way automatic switch ВА47-29/1/С6 | unit | 4 |  | 0
61 |  | Three-way automatic switch ВА47-29/1/C4 | unit | 3 |  | 0
62 |  | Three-way automatic switch ВА47-29/1/В4 | unit | 1 |  | 0
63 |  | Three-way automatic switch ВА47-29/1/С2 | unit | 9 |  | 0
64 |  | Three-way automatic switch ВА47-29/1/В2 | unit | 2 |  | 0
65 |  | Box К654У2 | unit | 1 |  | 0
66 |  | Power switch ВН-32-3Р-25А | unit | 1 |  | 0
67 |  | Contactor ПМА-0247 Uн=220В | unit | 13 |  | 0
68 |  | Mobile power generator with DIESSEL engine, n=9kVA, 220V/50hz; | compl. | 1 |  | 0
|  | External electrical network AEE |  |  |  | 0
|  | Chapter 1. Assembling works |  |  |  | 0
1 |  | In existing transformer station РУ-0,4 kV install |  |  |  | 0
2 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 1 |  | 0
3 | 08-02-472-1 | Ground binding conductors: Earth plug, horizontal round steel, diameter 12 mm (round steel) | 100 m | 0.09 |  | 0
4 | 08-02-471-4 | Earth plug, vertical, round steel, diameter 20 mm (round steel) | 10 units | 0.03 |  | 0
|  | Chapter 2. Construction works |  |  |  | 0
5 | 33-04-003-2 | Install reinforced concrete pillars LEA 0,38, 6-10 kV with sleepers without additives, with one pole СВ95 | unit | 6 |  | 0
6 | 33-04-008-3 | Mechanical suspension of isolated conductors LEA 0,38 kV СИП2а sec. 3х35+1х50mm2 | 1 km | 0.18 |  | 0
7 |  | Fittings for SIP |  |  |  | 0
8 |  | Stainless steel band F2007 | m | 16 |  | 0
9 |  | Clamps А200 | unit | 16 |  | 0
10 |  | Belt fastener CSB | unit | 18 |  | 0
11 |  | Support СА 1500 | unit | 8 |  | 0
12 |  | Anchoring fastener РА1500 | unit | 4 |  | 0
13 |  | Anchoring fastener РА25х100 | unit | 4 |  | 0
14 |  | Intermediate fastener ES-1500 | unit | 2 |  | 0
15 |  | Chapter 3. Equipment |  |  |  | 0
16 |  | Three-way automatic switch ВА47-29/3/С40 | unit | 1 |  | 0
Total VAT 0 rate | [5 empty] | 0

## ATM
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Installation of solid biomass heating system and solar panels for hot water production in kindergarten Speranta of Lozova village, Straseni district
Site: | y
Section: |  | Automated control and regulation system
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Assembling works |  |  |  | 0
1 | 11-02-002-01 | Device installed on flange mix, mass, kg, up to: 1,5 ТТУ, ТТП, ТПГ100эк | unit | 11 |  | 0
2 | 11-01-001-01 | Constructions for device installations, mass, kg, up to: 1 | unit | 9 |  | 0
3 | 11-02-001-01 | Device installed on threaded mix, mass, kg, up to: 1,5, (МП4, МВП, ДМ2010) | unit | 43 |  | 0
4 | 11-02-001-01 | Device installed on threaded mix, mass, kg, up to: 1,5, (draft gauge ТНМП-52-М2) | unit | 1 |  | 0
5 | 11-02-001-01 | Device installed on threaded mix, mass, kg, up to: 1,5 (gauge detector RGD COO MP1) | unit | 1 |  | 0
6 | 11-02-001-01 | Device installed on threaded mix, mass, kg, up to: 1,5 (electronic regulator Danfoss) | unit | 1 |  | 0
7 | 10-08-003-01 | Warning siren CC-1 | unit | 1 |  | 0
8 | 11-03-001-01 | Devices, installed on metallic constructions, panels and console: device, mass, kg, up to: 5 (detection device РОС-301) | unit | 2 |  | 0
9 | 11-02-002-01 | Device installed on flange mix, mass, kg, up to: 1,5 detection device ESM-10 | unit | 1 |  | 0
10 | 11-02-002-01 | Device installed on flange mix, mass, kg, up to: 1,5 detection device EMSU-10 | unit | 1 |  | 0
11 | 11-01-001-01 | Constructions for device installations, mass, kg, up to: 1 (tap) | unit | 50 |  | 0
12 | 11-06-002-04 | Electrical grid through tubes in panels and consoles: steel tubes D=15mm | 100 m | 0.22 |  | 0
13 | 08-02-407-6 | Steel pipe on constructions installed in priming channels executed on flooring support, diameter up to 20 mm | 100 m | 0.1 |  | 0
14 | 11-08-002-01 | Connection of electrical grid through pipes to devices: water-gas pipelines, diameter of conventional section, up to 15 mm | 10 unit | 0.44 |  | 0
15 | 08-02-411-1 | Metallic hose, outer diameter up to 15 mm (РЗ-ЦХ-Ш15) | 100 m | 0.46 |  | 0
16 | 10-06-034-14 | Various works: cable protection with plastic covers on wood or brick walls | m | 40 |  | 0
17 | 08-02-148-1 | Cable up to 35 kV in pipes, blocks and boxes, mass 1 m up to: 1 kg | 100 m | 2.78 |  | 0
18 | 08-02-412-9 | Introduce conductors in posed metallic pipes and hoses: each following mono- or multi-wire conductor in general mesh, summary section up to 6 mm2 ПВ1-0,38 sec.1x1,5 mm2 | 100 m | 0.16 |  | 0
19 |  | Warning and control panel ЩУС - box ЯУЭ-1263 dim. 1200x600x350 |  |  |  | 0
20 | 11-06-001-02 | Panel, mass, kg, up to: 100 size 1200х600х350 ЯУЭ1263 | unit | 1 |  | 0
21 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 86 |  | 0
22 | 11-08-001-04 | Connection of electrical grids to devices by glue | 100 unit. | 1.6 |  | 0
23 |  | Material costs |  |  |  | 0
24 |  | Selection device Г-16-225, В-16-225 | unit | 19 |  | 0
25 |  | Selection device Г16-80, В-16-80, 955-2 | unit | 19 |  | 0
26 |  | Steel pipe D=15mm | m | 22 |  | 0
27 |  | Steel pipe D=20mm | m | 10 |  | 0
28 |  | Metallic hose D=15mm | m | 36 |  | 0
29 |  | Cable КВВГнг-LS sect. 4х1,5mm2 | m | 40 |  | 0
30 |  | Cable КВВГнг-LS sect. 4х1,5mm2 | m | 136 |  | 0
31 |  | Cable КВВГнг-LS sect. 5х1,5mm2 | m | 120 |  | 0
32 |  | Cable КВВГнг-LS sect. 7х1,5mm2 | m | 22 |  | 0
33 |  | Conductor ПВ1-0,38sec. 1x1,5mm2 | m | 16 |  | 0
|  | Chapter 2. Equipment |  |  |  | 0
34 |  | Thermometer ТТУ, ТТП | unit | 9 |  | 0
35 |  | Thermometer ТПГ100эк-М1 | unit | 2 |  | 0
36 |  | Sensor relay level РОС-301 | unit | 2 |  | 0
37 |  | Manometer МП4-У, МВП-Ух0,6 | unit | 35 |  | 0
38 |  | Manometer ДМ2010С | unit | 8 |  | 0
39 |  | Detector CO RGD COOMP1 | unit | 1 |  | 0
40 |  | Sound alarm СС-1 | unit | 1 |  | 0
41 |  | Electronic temperature regulator Danfoss | unit | 1 |  | 0
42 |  | Membraneous draft gauge ТНМП-52-М2 | unit | 1 |  | 0
43 |  | Control panel and alarm ЩУС-ЯУЭ-1263 1200x600x350mm IP54 | unit | 1 |  | 0
44 |  | Relay ПЭ37 | unit | 28 |  | 0
45 |  | Relay РСВ19-11 | unit | 5 |  | 0
46 |  | Relay РСВ19-31 | unit | 2 |  | 0
47 |  | Automatic switch ВА47-29/1/С2 | unit | 6 |  | 0
48 |  | Contactor УП5311 | unit | 10 |  | 0
49 |  | Contactor УП5311 | unit | 1 |  | 0
50 |  | Warning device АD-22DS | unit | 13 |  | 0
51 |  | Diode Д246 | unit | 11 |  | 0
52 |  | Button ABLFS-22 | unit | 4 |  | 0
53 |  | Control block Бз24-4П | unit | 6 |  | 0
Total VAT 0 rate | [5 empty] | 0

## BK
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Installation of solid biomass heating system and solar panels for hot water production in kindergarten Speranta of Lozova village, Straseni district
Site: | y
Section: |  | Water and sewage
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | External water supply pipelines |  |  |  | 0
|  | Chapter 1. Mounting pipelines |  |  |  | 0
1 | TsC03B1 | Mechanical digging with excavator of 0,40-0,70 mc, with internal combustion engine and hydraulic control, in ground with natural humidity, unloading in piles ground category II | 100 m3 | 0.13 |  | 0
2 | TsA20B | Manual digging of soil, in slopes, holes dug with excavator or scraper, to fill in the digging of slope profile, in middle ground | m3 | 0.5 |  | 0
3 | TsD02A1 | Scattering loose soil from ground category I or II, executed by bulldozer on tracks 65-80 CP, in layers of 15-20 cm thickness | 100 m3 | 0.07 |  | 0
4 | TsD05A | Mechanical compacting with rammer of 150-200 kg of piles in successive layers of 20-30 cm thickness, excluding watering each layer in part, filling made of non-cohesive soil | 100 m3 | 0.07 |  | 0
5 | TsD01B | Scattering loose soil with spade, in uniform layers, of 10-30 cm thickness, in one throw up to 3 m from piles, including breaking the clots, soil from middle ground | m3 | 1.8 |  | 0
6 | TsD04B | Manual punning of piles made in horizontal or inclined digging at 1/4, including watering each soil layer in part with 10 cm thickness of cohesive soil | m3 | 1.8 |  | 0
7 | AcF03A | Filling the trenches for water and sewage pipelines, as sub-layer, protection layer, isolation layer or flange layer for drainage tubes, executed with sand | m3 | 0.6 |  | 0
8 | AcF03B | Filling the trenches for water and sewage pipelines, as sub-layer, protection layer, isolation layer or flange layer for drainage tube, executed with pearl gravel | m3 | 0.23 |  | 0
9 | AcE10A | Executing the manholes from ready-made reinforced concrete elements, for water supply circular (ring) with diameter 1,0 m, in soil without underground water | m3 | 0.77 |  | 0
10 | AcE10A1 | Ready-made reinforced concrete elements of valve manholes, circular (ring) with a diameter of 1,0 m for water supply, in soil without underground water . Note: resource with 0,00 (zero) norm is in accordance with the project | unit | 1 |  | 0
11 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment. | t | 0.02 |  | 0
12 | IzD04A | Painting metallic articles and constructions with oil paint in 2 layers, executed in profiles, with thickness between 8mm and 12mm inclusive, with hand brush | t | 0.02 |  | 0
13 | TsC54B | Broken stone foundation layer | m3 | 0.31 |  | 0
14 | DB16A | Asphalt concrete coat with small aggregates, executed at warm temperatures, in thickness of 2,5 cm manual laying | m2 | 3.08 |  | 0
15 | AcA52A | Polyethylene pipe, for water pipes embedded in trench, with diameter25 mm. Note: type of polyethylene pipe and warning band will be included according to the project PE80 SDR17,6 PN6 | m | 6 |  | 0
16 | AcF11C | Washing PVC, cast, cement, polyethylene pipes etc 20-75 mm, for drinking water after mounting and combining, before reception | m | 6 |  | 0
17 | AcF12A | Tightness test of polyethylene pipes mounted in trenches for water and sewage pipelines, with diameter up to 100 mm | m | 6 |  | 0
18 | AcB01A | Mounting fittings with manual or mechanical functioning (tubs, taps, vents), in water and sewage pipes, with diameter 25 mm (flange lock vent 15ч9р) | unit | 1 |  | 0
19 | AcA53A | Electrofusion mounting of fittings. Electro-fusion welding between polyethylene pipe and fitting (plugs, Tees, elbows)pipe with diameter 25 mm. Note: type of polyethylene fitting (plugs, Tees, elbows) will be included according to the project (saddle junction VALROM) | unit | 1 |  | 0
20 | AcA26A | Connecting the joint parts with flanges, flanges, including blind flanges and fittings, with diameter 25 mm (free flange) | unit | 2 |  | 0
21 | IC44B | Manufacture, mounting and cementing the pipes through walls, pipe with diameter 89х3,7 mm (sleeve L=0,30 m) | unit | 3 |  | 0
|  | External sewage pipelines |  |  |  | 0
22 | TsC03B1 | Mechanical digging with excavator of 0,40-0,70 mc, with internal combustion engine and hydraulic control, in ground with natural humidity, unloading in piles ground category II | 100 m3 | 0.25 |  | 0
23 | TsA20B | Manual digging of soil, in slopes, holes dug with excavator or scraper, to fill in the digging of slope profile, in middle ground | m3 | 0.8 |  | 0
24 | TsD02A1 | Scattering loose soil from ground category I or II, executed by bulldozer on tracks 65-80 CP, in layers of 15-20 cm thickness | 100 m3 | 0.14 |  | 0
25 | TsD05A | Mechanical compacting with rammer of 150-200 kg of piles in successive layers of 20-30 cm thickness, excluding watering each layer in part, filling made of non-cohesive soil | 100 m3 | 0.14 |  | 0
26 | TsD01B | Scattering loose soil with spade, in uniform layers, of 10-30 cm thickness, in one throw up to 3 m from piles, including breaking the clots, soil from middle ground | m3 | 3.5 |  | 0
27 | TsD04B | Manual punning of piles made in horizontal or inclined digging at 1/4, including watering each soil layer in part with 10 cm thickness of cohesive soil | m3 | 3.5 |  | 0
28 | AcF03A | Filling the trenches for water and sewage pipelines, as sub-layer, protection layer, isolation layer or finge layer for drainage tubes, executed with sand | m3 | 0.7 |  | 0
29 | AcF03B | Filling the trenches for water and sewage pipelines, as sub-layer, protection layer, isolation layer or finge layer for drainage tubes, executed with pearl gravel | m3 | 0.27 |  | 0
30 | AcE15A | Execution of manholes from ready-made reinforced concrete, for sewage, circular (rings) with diameter 2,0 m, in soil without underground water | m3 | 2.3 |  | 0
31 | AcE15A1 | Ready-made reinforced concrete elements, of manholes, circular (rings) with diameter 2,0 m, for sewage, in soil without underground water. Note: resource with 0,00 (zero) norm is in accordance with the project | unit | 1 |  | 0
32 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment. | t | 0.02 |  | 0
33 | IzD04A | Painting metallic articles and constructions with oil paint in 2 layers, executed in profiles, with thickness between 8mm and 12mm inclusive, with hand brush | t | 0.02 |  | 0
34 | CD50A | Plain brick masonry, format 250 x 120 x 65 in external walls with height up to 4 m | m3 | 0.05 |  | 0
35 | TsC54B | Broken stone foundation layer | m3 | 0.31 |  | 0
36 | DB16A | Asphalt concrete coat with small aggregates, executed at warm temperatures, in manual laying 2,5 cm thick | m2 | 3.08 |  | 0
37 | AcA07B | Mounting in the ground, outside buildings, PVC pipes type 4(G) or 3(M), with diameter 160 mm SN4 SDR41 | m | 3 |  | 0
38 | AcA07B | Mounting in the ground, outside buildings, PVC pipes type 4(G) or 3(M), with diameter 110 mm SN4 SDR41 | m | 5 |  | 0
39 | RCsU05B | Breaking the walls for pipes, in consolidations, walls from plain concrete with diameter up to 15 cm thick | unit | 1 |  | 0
40 | RCsU07C | Filling in the gaps in panels, with cement mortar, after installations | unit | 1 |  | 0
|  | Water pipe |  |  |  | 0
|  | Chapter 1. Sanitary works |  |  |  | 0
41 | SF51A | Water level measuring without meter, having the diameter of the branch 20 mm | set | 1 |  | 0
42 | SD19A | Straight-way valve with threaded sockets, with diameter 20 mm (stop valve 15Б1бк) | unit | 1 |  | 0
43 | SD18A | Garden hose pipe, mounted in the ground with diameter 15 mm | set | 1 |  | 0
44 | SA01B | Galvanized steel pipe for installations, mounted in industrial constructions, with diameter 20 mm | m | 6 |  | 0
45 | SA01A | Galvanized steel pipe for installations, mounted in industrial constructions, with diameter 15 mm | m | 2 |  | 0
46 | SF01A | Tightness test under pressure of hot or cold pipeline executed on steel, zinc pipelines, for installations, longitudinally welded, with diameter 3/8"-2" | m | 8 |  | 0
47 | SF05A | Washing hot or cold water pipelines, executed from steel, zinc pipes, with diameter 3/8"-2" | m | 8 |  | 0
48 | IzJ09B | Painting tin covers of pipelines and devices with oil paint in 2 layers, including priming | m2 | 0.6 |  | 0
49 | SD19A | Straight-way valve with threaded sockets, with diameter 15 mm | unit | 1 |  | 0
50 | AcA52A | Polyethylene pipe, for water pipes embedded in trench, with diameter25 mm. Note: type of polyethylene pipe and warning band will be included according to the project PE80 SDR21 PN6 | m | 3 |  | 0
51 | TsA03E | Manual digging of soil in limited spaces, under 1,00 m width, executed without supports, at inclined slope in foundations, trenches, etc., ground with average cohesion or very cohesive, up to 1,5 m depth middle ground | m3 | 1.4 |  | 0
52 | TsD01B | Scattering loose soil with spade, in uniform layers, of 10-30 cm thickness, in one throw up to 3 m from piles, including breaking the clots, soil from middle ground | m3 | 1.4 |  | 0
53 | TsD04B | Manual punning of piles made in horizontal or inclined digging at 1/4, including watering each soil layer in part with 10 cm thickness of cohesive soil | m3 | 1.4 |  | 0
54 | CA03F | Plain concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, Plain concrete class.... В7.5 | m3 | 0.06 |  | 0
|  | Chapter 2. Equipment |  |  |  | 0
55 |  | Cold water meter Dn15 mm | unit | 1 |  | 0
|  | Sewage pipe |  |  |  | 0
56 | SB08E | Pipe from plastic material for sewage, connected with rubber set, mounted apparently or under the flooring, with diameter 100 mm polypropylene | m | 15 |  | 0
57 | SB08C | Pipe from plastic material for sewage, connected with rubber set, mounted apparently or under the flooring, with diameter 50 mm polypropylene | m | 11 |  | 0
58 | SF04A | Tightening and functioning test of sewage system made of cast tubes, for drainage, vynil polychrome pipe, non-plasticised, light or from plastic material, ductile iron pipe with diameter up to 100 mm inclusive | 10 m | 2.6 |  | 0
59 | SB08E | Pipe from plastic material for sewage, connected with rubber set, mounted apparently or under the flooring, with diameter 100 mm (polypropylene fittings 15%) | m | 2.3 |  | 0
60 | SB08C | Pipe from plastic material for sewage, connected with rubber set, mounted apparently or under the flooring, with diameter 50 mm (polypropylene fittings 15%) | m | 1.65 |  | 0
61 | SB10E | Connecting part (plain ramification) from plastic material for sewage, combined with rubber, with diameter 100 mm (polyethylene review) | unit | 1 |  | 0
62 | SB10E | Connecting part (plain ramification) from plastic material for sewage, combined with rubber, with diameter 100 mm (polyethylene review) | unit | 2 |  | 0
63 | SB10C | Connecting part (plain ramification) from plastic material for sewage, combined with rubber, with diameter 50 mm (polyethylene review) | unit | 2 |  | 0
64 | SB10C | Connecting part (plain ramification) from plastic material for sewage, combined with rubber, with diameter 50 mm | unit | 7 |  | 0
65 | SB24E | Enamel iron flooring, simple, with diameter 100 mm (iron trap) | unit | 1 |  | 0
66 | AcA25A | Mounting through electric welding of connecting parts, of steel, in position, with diameter 100x50 mm (steel cone) | unit | 7 |  | 0
67 | CA03F | Plain concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, Plain concrete class.... В7.5 | m3 | 0.24 |  | 0
68 | SA40A | Installing anti-fire sockets fixed on the panel with dowels (anti-fire sleeve) | unit | 1 |  | 0
69 | SC06A | Dishwasher (with a compartment) for enamel cast iron, enamelled sheet, stainless steel, etc., with plastic drainpipe, mounted on consoles fixed on walls made of brick masonry | unit | 1 |  | 0
Total VAT 0 rate | [5 empty] | 0

## SIP
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Installation of solid biomass heating system and solar panels for hot water production in kindergarten Speranta of Lozova village, Straseni district
Site: | y
Section: |  | Anti fire system
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Assembling works |  |  |  | 0
1 | 10-08-002-03 | Automatic alarm PC: thermal, smoke, light, protection against explosion ИП-105-2/1 | unit | 4 |  | 0
2 | 10-08-002-05 | Automatic OC alarm: crash, without electromagnetic or piezoelectric contact, installed on glass ИПР-2-01 | unit | 1 |  | 0
3 | 10-08-001-06 | Receiving devices: Devices "ПС" for reception and control, warning. Concentrator: 4 ways main block (Varta 1/2 GSM) | unit | 1 |  | 0
4 | 10-08-019-01 | Various electric clock equipment: Wall mounted ramification box | unit | 1 |  | 0
5 | 10-08-003-01 | Warning device with the capacity SA-913F | unit | 1 |  | 0
6 | 08-02-148-1 | Cable up to 35 kV in pipes, blocks or boxes posed, mass 1 m up to: 1 kg КПСЭСнг(А)-FRLS 2x2x0,2 | 100 m | 0.3 |  | 0
7 | 08-02-148-1 | Cable up to 35 kV in pipes, blocks or boxes posed, mass 1 m up to: 1 kg ВВГнг-FRLS sec. 2х1,5mm2 | 100 m | 0.06 |  | 0
8 | 08-01-121-1 | Stationary acid accumulator, type: С-1, СК-1 1270 ВАТТ | unit | 1 |  | 0
9 | 10-08-019-01 | Various electric clock equipment: Wall mounted ramification box УК-2П | unit | 2 |  | 0
10 | 10-06-034-14 | Various works: cable protection with plastic gutters, on wood or brick walls ТМК-1020 | m | 36 |  | 0
|  | Chapter 2. Equipment |  |  |  | 0
11 |  | Heat and fire detectors (10% reserve) ИП-105-2/1 | unit | 4 |  | 0
12 |  | Fire detectors ИПР-2-01 | unit | 1 |  | 0
13 |  | Fire signal reception device Varta 1/2 GSM | unit | 1 |  | 0
14 |  | Metallic box | unit | 1 |  | 0
15 |  | Alarm system with flashing lights, 12V, SA-913F | unit | 1 |  | 0
16 |  | Accumulator 12V7Ah | unit | 1 |  | 0
16A |  | Fire extinguisher OP-5 | unit | 2 |  | 0
17 |  | Moto pump to extinguish the fire with water refilling debit 36 m3/hour and vacuum depth of 6 m, equipped with hose pipe d=50mm and length 60m, МН-13/60 or similar | unit | 1 |  | 0
Total VAT 0 rate | [5 empty] | 0

## FSS
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Installation of solid biomass heating system and solar panels for hot water production in kindergarten Speranta of Lozova village, Straseni district
Site: | y
Section: |  | Fuel system
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
0
0
Total VAT 0 rate | [5 empty] | 0

## Commiss
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Installation of solid biomass heating system and solar panels for hot water production in kindergarten Speranta of Lozova village, Straseni district
Site: | y
Commissioning
№ | Item | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
1 |  | Training of operators | course | 1 |  | 0
2 |  | Measure the emissions | test | 1 |  | 0
3 |  | Measure performance indicators | test | 1 |  | 0
4 |  | Commissioning integral system | system | 1 |  | 0
Total excluding VAT: | [5 empty] | 0
The bidder is responsible for any item that was not attributed a unit price and will be provided without additional costs for the UNDP

## Maintenance
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Installation of solid biomass heating system and solar panels for hot water production in kindergarten Speranta of Lozova village, Straseni district
Site: | y
Service and Maintenance works for 3-years of operation
№ | Item | Description of item | Periodicity | Quantity for 3 years | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
1 |  | Maintenance works and commissioning of heating system at the beginning of heating season | annual | 3 |  | 0
2 |  | Periodic maintenance works at the end of heating season | annual | 3 |  | 0
3 |  | Intervention and reparation of equipment in case of emergency | case | 3 |  | 0
4 |  | Telephonic assistance in using the system | permanent | 1 |  | 0
Total excluding VAT : | [5 empty] | 0
* Any equipment or component that requires replacement within the 3 years period and was not included in the list of wear parts shall be treated as a warranty case and must be provided by the contractor at no additional cost

## Boiler
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Installation of solid biomass heating system and solar panels for hot water production in kindergarten Speranta of Lozova village, Straseni district
Site: | y
Minimum specifications of boiler
No | Item | Requirements | Suggested requirements | Quantity | Unit price USD | Total, USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | Boiler | Boiler model: |  | 2 | 1 | 2
Fuel type: agro-pellets, type E, EN 14961-6 (according to Technical Specifications description) *
Limits of emission: EN 303-5:2012 Class 3
Q= 225 kW**
Productivity: minimum 80% ****
Work pressure: ≥1.5 bar
Maximum admitted temperature at operation:85 °C
Power tension: 230V/50Hz
Warranty for active components: 3 years
Warranty for passive components: 5 years
Burner cleaning: automatic cleaning system of burner through mechanical means
Diameter of smoke chimney 400mm ***:
Capacity of fuel tank: 800 L
Boiler assembling scheme in existing boiler room in accordance with the normative in force *****
Total excluding VAT : | [5 empty] | 2
* Specify type of fuel in accordance with the producer's recommendation
** Based on E type biofuel in accordance with the Technical Specifications Description.
*** The bidder may suggest a boiler with higher or lower diameter than specified in project documentation, provided that the smoke chimney is compatible with the boiler and ensures its optimal operation, and the costs are adjusted accordingly in financial offer.
**** Specify only numerical value. Do not include text
***** The bidder will include an illustration to show the location of boilers in the boiler room by indicating main dimensions