## ANNEX 3: TECHNICAL AND FINANCIAL OFFER - GOODS

Bidders are requested to complete this form, sign it and return it as part of their bid along with Annex 2: Quotation Submission Form. The Bidder shall fill in this form in accordance with the instructions indicated. No alterations to its format shall be permitted and no substitutions shall be accepted.

| Name of Bidder: | Click or tap here to enter text. |  |
| --- | --- | --- |
| RFQ reference: | RFQ22/02421: EU4MD/ Automated and intelligent systems for collecting and monitoring data and processes within the water supply and sewerage service in the Ungheni region | Date: Click or tap to enter a date. |

| Currency of the Quotation: USD United States Dollars INCOTERMS: DDP |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Item No | Description | UOM | Qty | Unit price | Total price |
| 1 | Meters • Meter type: Mechanical • Connection type: threaded, with mounting set and rubber seal • Nominal pressure: PN 16c • Must be: Dn-15mm, R not less than - 100 HV, L-110 mm, protected wheels, with mounting set and complete gaskets • Protection class IP-68 • Temperature class: cold water meter T30, T50 • Pressure loss class: ΔP 63 • Maximum measuring range Q3 / Q1: 160 • Length: 110 mm • Horizontal (H) or vertical (V) mounting position • Forged brass housing (mechanical) • Flow rate: Q3 -2.5 m³ / h - Flow profile sensitivity class: U0-D0 - The radio module (LoRa) or other variant of the module should be already embedded or even integrated - Allow operation in difficult working conditions (basement with high humidity, temperatures below 0 0 C, etc.) - They must be pre-equipped for remote transmission, without affecting the readability of the meter, readability must be ensured by mineral glass lenses, be resistant to scratches, ensure long-term operation and maintain all technical and metrological requirements - They must be provided with protection against falsification of the meter indications under the action of external permanent magnets - To be suitable for locations with various topologies, in urban and rural areas; apartments, residential area or public objectives - Allow reading, including meters installed in water chambers, basements or other hard-to-reach places, fountains with metal lids, the possibility of mounting in any position (vertical, horizontal) - Data storage and automatic retransmission on the same day or the next day in case of data transmission failuresBattery life of at least 10 years | item | 1000 |  |  |
| 2 | Software - The collection system must be provided and supplied with the meters, with the possibility of using it online by several users - The vendor will provide application usage licenses, database management and operating systems, and communications programs and interfaces provided - System applications, operating system, and communication software must be easily upgraded in the event of new releases - Possibility to exchange data with other systems or applications API or import / export structured files, ISON format, text file, Excel - The software will allow you to create reports on water consumption, bills and send them automatically to consumers - Data acquisition range from meters up to 3 km - Possess a high degree of accuracy in data processing - Alarm history along with its serial number - Possibility of later connection of additional smart meters to the existing data acquisition system The software will be installed at the buyer or in Cloud, with all access keys | item | 1 |  |  |
| 3 | Training of users - Staff training in meter installation, software operation, meter reprogramming - The contractor will carry out the training of the group of employees of at least 5 specialists within the enterprise, with a duration of about 2 hours | item | 1 |  |  |

Compliance with Requirements

|  | You Responses |  |  |
| --- | --- | --- | --- |
|  | Yes, we will comply | No, we cannot comply | If you cannot comply, pls. indicate counter - offer |
| Maximum delivery period not to exceed 60 calendar days upon signature of contract. | ☐ | ☐ | Click or tap here to enter text. |
| Minimum Technical Specifications | ☐ | ☐ | Click or tap here to enter text. |
| Delivery Term (INCOTERMS) | ☐ | ☐ | Click or tap here to enter text. |
| Minimum 24 months of warranty The provider undertakes to remove, on its own account, all defects caused by it and / or in the case of the use of non-quality materials, detected during the warranty period; The provider will ensure, free of charge, during the warranty period, the repair of defects and spare parts within a maximum of 48 hours from the notification. | ☐ | ☐ | Click or tap here to enter text. |
| Delivery and testing | ☐ | ☐ | Click or tap here to enter text. |
| Authorized Service Centre to be provided | ☐ | ☐ | Click or tap here to enter text. |
| Validity of Quotation 90 calendar days | ☐ | ☐ | Click or tap here to enter text. |
| Payment terms | ☐ | ☐ | Click or tap here to enter text. |
| All Provisions of the UNDP General Terms and Conditions | ☐ | ☐ | Click or tap here to enter text. |

| I, the undersigned, certify that I am duly authorized to sign this quotation and bind the company below in event that the quotation is accepted. |  |
| --- | --- |
| Exact name and address of company Company NameClick or tap here to enter text. Address: Click or tap here to enter text. Click or tap here to enter text. Phone No.: Click or tap here to enter text. Email Address: Click or tap here to enter text. | Authorized Signature: Date: Click or tap here to enter text. Name: Click or tap here to enter text. Functional Title of Authorised Signatory: Click or tap here to enter text. Email Address: Click or tap here to enter text. |