Annex 2: Technical Responsiveness Table

| Item No | Requested Specifications |  | Technical compliance (yes/no) | Offered specifications (Please provide detailed description/ specifications for each of the items listed below) Please insert brand name details, Provide leaflet, catalogue links |
| --- | --- | --- | --- | --- |
| SCHEDULE NO.1 - PLANT AND EQUIPMENT, INCLUDING MANDATORY SPARE PARTS |  |  |  |  |
| 1. | CENTRAL DISPATCH AND CONTROL OFFICE (DCO) |  |  |  |
| 1.1 | Rack IT Enclosure incl. passive elements (accessories) - Sheet steel – aluminum. - 85% of vented surface area - Width: 800mm; Height: 2000mm; Depth: 800mm. - The industry standard rack cabinet - 42U, 19” of racks - Load capacity of minimum 15000N - All needed accessories for mounting. For detailed requirements see chapter 3.1.1 of Annex 1 |  |  | Manufacturer: Model: |
| 1.2 | Server - Form factor/height 2U Rack. - Processor CPU Xeon® (or equivalent). - Memory 32 GB DDR4. - SSD 2x256GB in RAID-1 as a boot disk. - HDD 2x1.2TB 12Gbps. - RAID 5 configuration support. - Power supply 2xPSU, redundant 550 W AC. - Network interface 1 x IMM and 4 × 1 Gb. - Platform Module built-in USB Ports / VGA Ports Up to 3 front (1 x USB 3.0, 2 x USB 2.0) and 4, 1 internal (USB 3.0) / 1 front and 1 back - Server shall be from the same manufacturer as all workstations - Operating System: - Windows® Server x64 bit – English. - Licenses - Windows® Server x64 bit– Multilanguage. - Microsoft ® Office tools: Office Home & Business 2023 64 English or higher. - Limited warranty 3-year and upgrades available. For detailed requirements see chapter 3.1.2 of Annex 1 |  |  | Manufacturer: Model: |
| 1.3 | Network hardware (VPN Router, Ethernet Swich) - 19” Rack-mount VPN router. - Minimum of 600 MHz CPU speed. - Minimum of 128 Mb RAM. - Max. concurrent IPsec VPN tunnels – 100. - Max. concurrent SSL VPN users – 25. - Minimum of 4x 1Gb/s Ethernet ports; 1x1Gb/s WAN port. - All needed accessories for mounting in server enclosures. For detailed requirements see chapter 3.1.3 of Annex 1 |  |  | Manufacturer: Model: |
| 1.4 | Uninterruptible power supply UPS - The UPS shall ensure minimum of 1-hour backup time of both redundancy servers. - Form factor: 2U Rack. - At least 5000VA. - 160 to 280 VAC Input with automatic 50/60 detection, with full time multi-pole noise filtering, 0.3% IEEE surge let through, zero clamping response time. - The UPS shall have audible alarms, automatic internal bypass, and automatic load restart after UPS shutdown, automatic self-test, and predictive failure notification. - Continuous battery recharging, even if the power button is set to OFF. The UPS shall have a battery replacement indicator, disconnected battery notification, and shall allow batteries to be replaced with equipment energized. - The UPS shall have a USB port and communications cable for connection to the workstation. The UPS shall have a power management software package suitable for Windows. - WEB/SNMP connectivity device. - All needed accessories for connection of both servers. For detailed requirements see chapter 3.1.4 of Annex 1 |  |  | Manufacturer: Model: |
| 1.5 | Operator Workstation - Processor: i5 Core last generation. - Operating System: Windows® 11 Professional. - Video Card: External 3 GB, Three Monitor, 2 DP & 1 DVI. Graphics card suitable to handle the graphics of the SCADA application. - Memory: 16GB, DDR4. - Optical Drive: 16X DVD+/-RW and 8X DVD - SSD 1x256GB as a boot disk - Hard Drive: 500GB, 7200 RPM, 3.5” SATA 6Gb/s, Due to working permanently (mode 24/7) Primary Operator Workstation shall be supplied with the Industrial Hard Drive with more industry leading speeds, performance, and reliability. - Network Adapter: 1GbE NIC, Dual Port. - At least three (3) USB ports. - 3xMonitor: Minimum 27-inch full QHD screen, VGA/DVI with incorporated speakers (3 monitors for Primary Operator Workstation). - Keyboard: USB Entry Quiet key, No Hot Keys. - Mouse: USB Optical Mouse with scroll, All Black Design with mouse pad. - UPS 1000VA. - Productivity software for PC shall be Microsoft® Office Business Edition. - 1xLaser printer, color, with A4 paper format. - Workstation shall be from the same manufacturer as server The Operator Workstations shall be supplied with preinstalled system and all configured drivers. For detailed requirements see chapter 3.2 of Annex 1 |  |  | Manufacturer: Model: |
| 1.6 | Engineer Workstation - Processor: Core i5 last generation. - Operating System: Windows® 11 Professional. - Video Card: External 3 GB, Three Monitor, 2 DP & 1 DVI. Graphics card suitable to handle the graphics of the SCADA application. - Memory: 16GB, DDR4. - Optical Drive: 16X DVD+/-RW and 8X DVD. - SSD 1x256GB as a boot disk. - Hard Drive: 500GB, 7200 RPM, 3.5” SATA 6Gb/s. - Network Adapter: 1 GbE NIC, Dual Port. - At least three (3) USB ports. - 1xMonitor: Minimum 27-inch full QHD screen. - Keyboard: USB Entry Quiet key, No Hot Keys. - Mouse: USB Optical Mouse with scroll, All Black Design w/mouse pad. - UPS 1000VA. - Productivity software for PC shall be Microsoft® Office Business Edition. - Workstation shall be from the same manufacturer as server The Engineer Workstation shall be supplied with preinstalled system and all configured drivers. For detailed requirements see chapter 3.3 of Annex 1 |  |  | Manufacturer: Model: |
| 1.7 | SCADA Software for server The SCADA software shall have the following minimum features: - Open system architecture with relational database management system. - Feature for checking the healthiness of the system and communication links. - Sufficient capacity in terms of memory and I/O to perform the required functions. - User-friendliness using ‘Windows’ based applications. - Keeping of statistics of errors encountered in communication. - Prioritization of tasks like alarm processing. - Database for storing and retrieval of various parameters, historical data etc. - Historical data archiving on hard disk as well as on removable media for at least 5 years. Multiple levels of security for users with predefined access rights and password protected access. Alarm generation with timestamping. - Trending of real-time and historical data in different user configurable formats. - Flexible reporting system providing pre-formatted standard reports for common requirements as well as generation of free format reports configurable by the user, available on demand, event/ application initiation or at pre-set time intervals. - Information display in various formats including bar graph, chart etc. - Allows to configure and update remote firmware of field equipment (PLCs/ RTUs). - Allow operation in a redundant system. - Possibility of mobile client integration. Web services for 2 (two) web browser-based clients. - Historian part will have to be included. - Contains an integrated GIS system. - In the event of a communication interruption with the field equipment, the system will store the data locally on the PLC/RTU, following which the SCADA will recover them when the communication returns in a transparent and secure manner. All Software specifications and licenses shall be ready installed and additionally delivered on licensed DVD/CD to the Employer. For detailed requirements see chapter 3.4 of Annex 1 |  |  |  |
| 1.8 | SCADA Software for Operator Workstation For detailed requirements see chapter 3.5 of Annex 1 |  |  |  |
| 1.9 | SCADA development software for engineer workstation For detailed requirements see chapter 3.6 of Annex 1 |  |  |  |
| 2. | STATIONS |  |  |  |
| 2.1 | Local Data Acquisition and Control Equipment for PS-1 (Stația de Pompare Treapta I) - Wall mounted panel (incl. Mounted accessories and necessary wiring). - PLC with all necessary modules (please refer to particular specification). - In case if the station does not have Ethernet TCP/IP connection, the Local equipment shall be supplied with GPRS router. The strength of the GPRS signal shall be ensured by the Employer. - HMI (please refer to particular specification). - UPS for backup power in case of loose main power. - Measurement equipment (See chapter 5.1.1 of Annex 1) - All necessary consumable for installation. For detailed requirements see chapter 4 and 5 of Annex 1 |  |  | Manufacturer: Model: |
| 2.2 | Local Data Acquisition and Control Equipment for PS-2 (Stația de Pompare Treapta II) - Wall mounted panel (incl. Mounted accessories and necessary wiring). - PLC with all necessary modules (please refer to particular specification). - In case if the station does not have Ethernet TCP/IP connection, the Local equipment shall be supplied with GPRS router. The strength of the GPRS signal shall be ensured by the Employer. - HMI (please refer to particular specification). - UPS for backup power in case of loose main power. - Measurement equipment (See chapter 5.1.2 of Annex 1) - All necessary consumable for installation. For detailed requirements see chapter 4 and 5 of Annex 1 |  |  | Manufacturer: Model: |
| 2.3 | Local Data Acquisition and Control Equipment for WTP (Stația de tartare) - Wall mounted panel (incl. Mounted accessories and necessary wiring). - PLC with all necessary modules (please refer to particular specification). - In case if the station does not have Ethernet TCP/IP connection, the Local equipment shall be supplied with GPRS router. The strength of the GPRS signal shall be ensured by the Employer. - HMI (please refer to particular specification). - UPS for backup power in case of loose main power. - Measurement equipment (See chapter 5.2 of Annex 1.) - All necessary consumable for installation. For detailed requirements see chapter 4 and 5 of Annex 1 |  |  | Manufacturer: Model: |
| 2.4 | Local Data Acquisition and Control Equipment for BPS-1 (str. Nicolae Iorga) - Wall mounted panel (incl. Mounted accessories and necessary wiring). - PLC with all necessary modules (please refer to particular specification). - In case if the station does not have Ethernet TCP/IP connection, the Local equipment shall be supplied with GPRS router. The strength of the GPRS signal shall be ensured by the Employer. - HMI (please refer to particular specification). - UPS for backup power in case of loose main power. - Measurement equipment (See chapter 5.3.1 of Annex 1.) - All necessary consumable for installation. For detailed requirements see chapter 4 and 5 of Annex 1. |  |  | Manufacturer: Model: |
| 2.5 | Local Data Acquisition and Control Equipment for BPS-2 (str. Romană 26) - Wall mounted panel (incl. Mounted accessories and necessary wiring). - PLC with all necessary modules (please refer to particular specification). - In case if the station does not have Ethernet TCP/IP connection, the Local equipment shall be supplied with GPRS router. The strength of the GPRS signal shall be ensured by the Employer. - HMI (please refer to particular specification). - UPS for backup power in case of loose main power. - Measurement equipment (See chapter 5.3.2 of Annex 1.) - All necessary consumable for installation. For detailed requirements see chapter 4 and 5 of Annex 1 |  |  | Manufacturer: Model: |
| 2.6 | Local Data Acquisition and Control Equipment for BPS-3 (str. Romană 66) - Wall mounted panel (incl. Mounted accessories and necessary wiring). - PLC with all necessary modules (please refer to particular specification). - In case if the station does not have Ethernet TCP/IP connection, the Local equipment shall be supplied with GPRS router. The strength of the GPRS signal shall be ensured by the Employer. - HMI (please refer to particular specification). - UPS for backup power in case of loose main power. - Measurement equipment (See chapter 5.3.3 of Annex 1.) - All necessary consumable for installation. For detailed requirements see chapter 4 and 5 of Annex 1. |  |  | Manufacturer: Model: |
| 2.7 | Local Data Acquisition and Control Equipment for BPS-4 (str. Națională 33) - Wall mounted panel (incl. Mounted accessories and necessary wiring). - PLC with all necessary modules (please refer to particular specification). - In case if the station does not have Ethernet TCP/IP connection, the Local equipment shall be supplied with GPRS router. The strength of the GPRS signal shall be ensured by the Employer. - HMI (please refer to particular specification). - UPS for backup power in case of loose main power. - Measurement equipment (See chapter 5.3.4 of Annex 1.) - All necessary consumable for installation. For detailed requirements see chapter 4 and 5 of Annex 1. |  |  | Manufacturer: Model: |
| 2.8 | Local Data Acquisition and Control Equipment for BPS-5 (str. Romană 112) - Wall mounted panel (incl. Mounted accessories and necessary wiring). - PLC with all necessary modules (please refer to particular specification). - In case if the station does not have Ethernet TCP/IP connection, the Local equipment shall be supplied with GPRS router. The strength of the GPRS signal shall be ensured by the Employer. - HMI (please refer to particular specification). - UPS for backup power in case of loose main power. - Measurement equipment (See chapter 5.3.5 of Annex 1.) - All necessary consumable for installation. For detailed requirements see chapter 4 and 5 of Annex 1. |  |  | Manufacturer: Model: |
| 2.9 | Local Data Acquisition and Control Equipment for BPS-6 (str. Ungureanu 9) - Wall mounted panel (incl. Mounted accessories and necessary wiring). - PLC with all necessary modules (please refer to particular specification). - In case if the station does not have Ethernet TCP/IP connection, the Local equipment shall be supplied with GPRS router. The strength of the GPRS signal shall be ensured by the Employer. - HMI (please refer to particular specification). - UPS for backup power in case of loose main power. - Measurement equipment (See chapter 5.3.6 of Annex 1.) - All necessary consumable for installation. For detailed requirements see chapter 4 and 5 of Annex 1 |  |  | Manufacturer: Model: |
| 2.10 | Local Data Acquisition and Control Equipment for BPS-7 (str. Cristiuc 11) - Wall mounted panel (incl. Mounted accessories and necessary wiring). - PLC with all necessary modules (please refer to particular specification). - In case if the station does not have Ethernet TCP/IP connection, the Local equipment shall be supplied with GPRS router. The strength of the GPRS signal shall be ensured by the Employer. - HMI (please refer to particular specification). - UPS for backup power in case of loose main power. - Measurement equipment (See chapter 5.3.7 of Annex 1.) - All necessary consumable for installation. For detailed requirements see chapter 4 and 5 of Annex 1. |  |  | Manufacturer: Model: |
| 2.11 | Local Data Acquisition and Control Equipment for BPS-8 (str. Boico 5-7) - Wall mounted panel (incl. Mounted accessories and necessary wiring). - PLC with all necessary modules (please refer to particular specification). - In case if the station does not have Ethernet TCP/IP connection, the Local equipment shall be supplied with GPRS router. The strength of the GPRS signal shall be ensured by the Employer. - HMI (please refer to particular specification). - UPS for backup power in case of loose main power. - Measurement equipment (See chapter 5.3.8 of Annex 1) - All necessary consumable for installation. For detailed requirements see chapter 4 and 5 of Annex 1. |  |  | Manufacturer: Model: |
| 2.12 | Local Data Acquisition and Control Equipment for BPS-9 (str. Porumbescu 3) - Wall mounted panel (incl. Mounted accessories and necessary wiring). - PLC with all necessary modules (please refer to particular specification). - In case if the station does not have Ethernet TCP/IP connection, the Local equipment shall be supplied with GPRS router. The strength of the GPRS signal shall be ensured by the Employer. - HMI (please refer to particular specification). - UPS for backup power in case of loose main power. - Measurement equipment (See chapter 5.3.9 of Annex 1.) - All necessary consumable for installation. For detailed requirements see chapter 4 and 5 of Annex 1. |  |  | Manufacturer: Model: |
| 2.13 | Local Data Acquisition and Control Equipment for WWPS-1 (SPAU-1) – (str. Tereza Sobolevschi) - Wall mounted panel (incl. Mounted accessories and necessary wiring). - PLC with all necessary modules (please refer to particular specification). - In case if the station does not have Ethernet TCP/IP connection, the Local equipment shall be supplied with GPRS router. The strength of the GPRS signal shall be ensured by the Employer. - HMI (please refer to particular specification). - UPS for backup power in case of loose main power. - Measurement equipment. (See chapter 5.4.1 of Annex 1.) - All necessary consumable for installation. For detailed requirements see chapter 4 and 5 of Annex 1. |  |  | Manufacturer: Model: |
| 2.14 | Local Data Acquisition and Control Equipment for WWPS-2 (SPAU-2) – (str. Cetireni) - Wall mounted panel (incl. Mounted accessories and necessary wiring). - PLC with all necessary modules (please refer to particular specification). - In case if the station does not have Ethernet TCP/IP connection, the Local equipment shall be supplied with GPRS router. The strength of the GPRS signal shall be ensured by the Employer. - HMI (please refer to particular specification). - UPS for backup power in case of loose main power. - Measurement equipment. (See chapter 5.4.2 of Annex 1.) - All necessary consumable for installation. For detailed requirements see chapter 4 and 5 of Annex 1. |  |  | Manufacturer: Model: |
| 2.15 | Local Data Acquisition and Control Equipment for WWPS-3 (SPAU-3) – (str. Ion Neculce) - Wall mounted panel (incl. Mounted accessories and necessary wiring). - PLC with all necessary modules (please refer to particular specification). - In case if the station does not have Ethernet TCP/IP connection, the Local equipment shall be supplied with GPRS router. The strength of the GPRS signal shall be ensured by the Employer. - HMI (please refer to particular specification). - UPS for backup power in case of loose main power. - Measurement equipment. (See chapter 5.4.3 of Annex 1.) - All necessary consumable for installation. For detailed requirements see chapter 4 and 5 of Annex 1. |  |  | Manufacturer: Model: |
| 2.16 | Local Data Acquisition and Control Equipment for WWPS-4 (str. Ungureanu 15) - Wall mounted panel (incl. Mounted accessories and necessary wiring). - PLC with all necessary modules (please refer to particular specification). - In case if the station does not have Ethernet TCP/IP connection, the Local equipment shall be supplied with GPRS router. The strength of the GPRS signal shall be ensured by the Employer. - HMI (please refer to particular specification). - UPS for backup power in case of loose main power. - Measurement equipment. (See chapter 5.4.4 of Annex 1.) - All necessary consumable for installation. For detailed requirements see chapter 4 and 5 of Annex 1. |  |  | Manufacturer: Model: |
| 2.17 | Local Data Acquisition and Control Equipment for WWPS-5 (str. Decebal 71) - Wall mounted panel (incl. Mounted accessories and necessary wiring). - PLC with all necessary modules (please refer to particular specification). - In case if the station does not have Ethernet TCP/IP connection, the Local equipment shall be supplied with GPRS router. The strength of the GPRS signal shall be ensured by the Employer. - HMI (please refer to particular specification). - UPS for backup power in case of loose main power. - Measurement equipment (See chapter 5.4.5 of Annex 1.) - All necessary consumable for installation. For detailed requirements see chapter 4 and 5 of Annex 1. |  |  | Manufacturer: Model: |
| 2.18 | Local Data Acquisition and Control Equipment for WWPS-6 (str. Burebista 17) - Wall mounted panel (incl. Mounted accessories and necessary wiring). - PLC with all necessary modules (please refer to particular specification). - In case if the station does not have Ethernet TCP/IP connection, the Local equipment shall be supplied with GPRS router. The strength of the GPRS signal shall be ensured by the Employer. - HMI (please refer to particular specification). - UPS for backup power in case of loose main power. - Measurement equipment. (See chapter 5.4.6 of Annex 1.) - All necessary consumable for installation. For detailed requirements see chapter 4 and 5 of Annex 1 |  |  | Manufacturer: Model: |
| 2.19 | Local Data Acquisition and Control Equipment for WWPS-7 (str. Caragiale 3-5) - Wall mounted panel (incl. Mounted accessories and necessary wiring). - PLC with all necessary modules (please refer to particular specification). - In case if the station does not have Ethernet TCP/IP connection, the Local equipment shall be supplied with GPRS router. The strength of the GPRS signal shall be ensured by the Employer. - HMI (please refer to particular specification). - UPS for backup power in case of loose main power. - Measurement equipment. (See chapter 5.4.7 of Annex 1.) - All necessary consumable for installation. For detailed requirements see chapter 4 and 5 of Annex 1. |  |  | Manufacturer: Model: |
| 2.20 | Local Data Acquisition and Control Equipment for WWPS-8 – str. Lacului - Wall mounted panel (incl. Mounted accessories and necessary wiring). - PLC with all necessary modules (please refer to particular specification). - In case if the station does not have Ethernet TCP/IP connection, the Local equipment shall be supplied with GPRS router. The strength of the GPRS signal shall be ensured by the Employer. - HMI (please refer to particular specification). - UPS for backup power in case of loose main power. - Measurement equipment. (See chapter 5.4.8 of Annex 1.) - All necessary consumable for installation. For detailed requirements see chapter 4 and 5 of Annex 1. |  |  | Manufacturer: Model: |
| 2.21 | Local Data Acquisition and Control Equipment for MWWPS (SPPAU) - Wall mounted panel (incl. Mounted accessories and necessary wiring). - PLC with all necessary modules (please refer to particular specification). - In case if the station does not have Ethernet TCP/IP connection, the Local equipment shall be supplied with GPRS router. The strength of the GPRS signal shall be ensured by the Employer. - HMI (please refer to particular specification). - UPS for backup power in case of loose main power. - Measurement equipment. (See chapter 5.4.9 of Annex 1.) - All necessary consumable for installation. For detailed requirements see chapter 4 and 5 of Annex 1 |  |  | Manufacturer: Model: |
| 3. | MANDATORY SPARE PARTS |  |  |  |
| 3.1 | PLC + DI + AI (Programmable logic controller + digital input module + analogic input module For detailed requirements see chapter 4.12 of Annex 1 |  |  |  |
| 3.2 | HMI (Human machine interface) For detailed requirements see chapter 4.13 of Annex 1 |  |  |  |
| 3.3 | Pressure transmitter - Type of sensor: ceramic. - Measuring range: suction pipe: 0…10 bar, pressure pipe: 0…16 bar. - Water hammer protection: yes. - Ambient temperature for probe: -30 °C +50 °C. - Ambient temperature for converter: +5 °C +50 °C. - Fluid temperature: 0 °C +50 °C. - Media resistance: high. - Media environment: water. - Protection class: IP 67. - Accuracy: 0.5%. - Power supply: 12/24 (24VDC) for probe. - Output signal: 4-20 mA. - Standards and Guidelines: DIN EN 60770 (IEC 60770); DIN EN 61003-1. - Edition: 1993-12; IEC 60529; DIN 16086. - Each pressure transmitter shall be accompanied in a set with a pressure shocks absorber. - Material of housing: anticorrosive steel. - Max. operating and storage temperature: +95°C. - Max. operating pressure: Pmax 70 MPa. For detailed requirements see chapter 4.15 of Annex 1 |  |  | Manufacturer: Model: |
| SCHEDULE NO.2 - INSTALLATION AND OTHER SERVICES |  |  |  |  |
| Item No |  | Minimum requirements | Technical compliance (yes/no) | Offered specifications (Please confirm that the offered design and stations will meet the requirements of Annex 1) |
| 1. |  | CENTRAL DISPATCH AND CONTROL OFFICE (DCO) |  |  |
| 1.1 |  | Detailed design of SCADA system to central DCO For detailed requirements see chapter 2 of Annex 1 |  |  |
| 1.2 |  | Detailed design of SCADA system at facilities For detailed requirements see chapter 2 of Annex 1 |  |  |
| 1.3 |  | Installation and development of SCADA Server software applications according to beneficiary requirements For detailed information see Annex 1 |  |  |
| 1.4 |  | Installation of SCADA Server Equipment to Central DCO For detailed requirements see chapter 6.7 of Annex 1. |  |  |
| 1.5 |  | Installation of SCADA software for Operator and Engineer Workstation according to beneficiary requirements For detailed requirements see chapter 6.7 of Annex 1. |  |  |
| 2. |  | STATIONS |  |  |
| 2.1 |  | Local Data Acquisition and Control Equipment for PS-1 (Stația de Pompare Treapta I) For detailed requirements see chapter 5 and 6.8 of Annex 1 |  |  |
| 2.2 |  | Local Data Acquisition and Control Equipment for PS-2 (Stația de Pompare Treapta II) For detailed requirements see chapter 5 and 6.8 of Annex 1 |  |  |
| 2.3 |  | Local Data Acquisition and Control Equipment for WTP (Stația de tartare) For detailed requirements see chapter 5 and 6.8 of Annex 1 |  |  |
| 2.4 |  | Local Data Acquisition and Control Equipment for BPS-1 (str. Nicolae Iorga) For detailed requirements see chapter 5 and 6.8 of Annex 1 |  |  |
| 2.5 |  | Local Data Acquisition and Control Equipment for BPS-2 (str. Romană 26) For detailed requirements see chapter 5 and 6.8 of Annex 1 |  |  |
| 2.6 |  | Local Data Acquisition and Control Equipment for BPS-3 (str. Romană 66) For detailed requirements see chapter 5 and 6.8 of Annex 1 |  |  |
| 2.7 |  | Local Data Acquisition and Control Equipment for BPS-4 (str. Națională 33) For detailed requirements see chapter 5 and 6.8 of Annex 1 |  |  |
| 2.8 |  | Local Data Acquisition and Control Equipment for BPS-5 (str. Romană 112) For detailed requirements see chapter 5 and 6.8 of m Annex 1 |  |  |
| 2.9 |  | Local Data Acquisition and Control Equipment for BPS-6 (Ungureanu 9) For detailed requirements see chapter 5 and 6.8 of Annex 1 |  |  |
| 2.10 |  | Local Data Acquisition and Control Equipment for BPS-7 (str. Cristiuc 11) For detailed requirements see chapter 5 and 6.8 of Annex 1 |  |  |
| 2.11 |  | Local Data Acquisition and Control Equipment for BPS-8 (str. Boico 5-7) For detailed requirements see chapter 5 and 6.8 of Annex 1 |  |  |
| 2.12 |  | Local Data Acquisition and Control Equipment for BPS-9 (str. Porumbescu 3) For detailed requirements see chapter 5 and 6.8 of Annex 1 |  |  |
| 2.13 |  | Local Data Acquisition and Control Equipment for WWPS-1 (SPAU-1) – (str. Tereza Sobolevschi) For detailed requirements see chapter 5 and 6.8 of Annex 1 |  |  |
| 2.14 |  | Local Data Acquisition and Control Equipment for WWPS-2 (SPAU-2) – (str. Cetireni) For detailed requirements see chapter 5 and 6.8 of Annex 1 |  |  |
| 2.15 |  | Local Data Acquisition and Control Equipment for WWPS-3 (SPAU-3) – (str. Ion Neculce) For detailed requirements see chapter 5 and 6.8 of Annex 1 |  |  |
| 2.16 |  | Local Data Acquisition and Control Equipment for WWPS-4 – (str. Ungureanu 15) For detailed requirements see chapter 5 and 6.8 of Annex 1 |  |  |
| 2.17 |  | Local Data Acquisition and Control Equipment for WWPS-5 (str. Decebal 71) For detailed requirements see chapter 5 and 6.8 of Annex 1 |  |  |
| 2.18 |  | Local Data Acquisition and Control Equipment for WWPS-6 (str. Burebista 17) For detailed requirements see chapter 5 and 6.8 of Annex 1 |  |  |
| 2.19 |  | Local Data Acquisition and Control Equipment for WWPS-7 (str. Caragiale 3-5) For detailed requirements see chapter 5 and 6.8 of Annex 1 |  |  |
| 2.20 |  | Local Data Acquisition and Control Equipment for WWPS-8 (str. Lacului) For detailed requirements see chapter 5 and 6.8 of Annex 1 |  |  |
| 2.21 |  | Local Data Acquisition and Control Equipment for MWWPS (SPPAU) For detailed requirements see chapter 5 and 6.8 of Annex 1 |  |  |