ANNEX B: TERMS OF REFERENCE

# for

Procurement of Engineering Services for Rehabilitation of WASH facilities in 21 schools in Moldova (Package 6)

- BACKGROUND

    - UNICEF Moldova signed a work plan with the Ministry of Education and Research recently, and one of the key agenda of the work plan is to improve water, sanitation, and hygiene (WASH) services in schools. Therefore, UNICEF Moldova supports the Moldovan authorities to provide WASH services in schools and enhance early Intervention systems and services for Moldovan and refugee children from Ukraine.

    - To that aim, UNICEF Moldova will conduct the assessment and rehabilitate/construct climate-resilient, energy-efficient, and environment-friendly WASH infrastructure in educational institutions, as detailed in the Scope of the Work below.

    - This project is expected to benefit more than 30,000 children by providing access to safe water and sanitation services annually, which is a fundamental right that safeguards health and human dignity.

    - The objective of these Terms of Reference is to guide a bidding exercise to identify suitable engineering firm for the procurement of engineering services required for this construction project.

- DEFINITION

  - Renovation of a building refers to the demolition & reconstruction work within the existing building, mentioned below as generic items. They will vary based on the specific needs of each building.

  - Rehabilitation of WASH facilities (Water, Sanitation, and Hygiene) refers to the process of restoring or improving existing water, sanitation, and hygiene infrastructure to ensure their functionality, safety, and effectiveness. The process includes also renewing flooring, walls, and ceilings, and ensuring that all fixtures and fittings meet current health, safety, and accessibility standards.

  - Design documentation refers to the set of technical documents that includes the detailed design drawing, (architectural, structural, mechanical, electrical, and plumbing drawings and other compartments), instructions and specifications necessary to perform the construction project.

  - Cost estimates and BoQ are documents used to appreciate the costs of materials, labour, and other resources required for a construction project. The cost estimates documentation includes detailed breakdowns of costs for each compartment of the project, while the BoQ provides a list with all types of works, quantities, and unit prices needed for the project.

  - Construction of new buildings refers to the construction of an independent built structure.

  - Construction of a new annex to the existing building refers to the construction of an additional structure that is physically connected to the current building to expand the usable space of the existing building while maintaining structural integrity, aesthetic coherence, and functional integration.

  - Connection of facilities to centralized water supply and sewage systems refers to the process of integrating a building internal water distribution and sewage systems with the existing municipal or centralized networks.

  - External Service Design refers to the process of planning and creating the infrastructure and networks outside a building to support its functionality. This includes the design of external systems (water supply pipelines, sewage systems, stormwater drainage, electrical power supply, and communication networks) to ensures that the building is connected to municipal or regional utility services and complies with all relevant codes and standards.

  - Internal Service Design refers to the process of planning and creating the infrastructure and networks inside a building to support its functionality and meet the needs of its users. This includes the design of internal systems such as plumbing, electrical wiring, HVAC, lighting, and communication systems. Internal service design ensures that the building’s internal services are efficiently and safely integrated, adhering to all relevant codes and standards.

- SCOPE OF SERVICES

  - The scope of engineering services is divided in 2 packages: Package 1 includes site assessment, design and technical documents, preparation of cost estimates and BoQ sets, technical support to procurement and author supervision services; and Package 2 includes quality assurance and site supervision. Each package is described in detail in Section 4 Expected Deliverables.

  - The Package 1 is divided into two sub-packages including following locations of intervention:

Sub-Package 1.1 Rehabilitation of the existing WASH facilities within the building and adapting them to meet the needs of people with disabilities as well as construction of new facilities in a dedicated space within the building (by specific case). External works including installation of the WWTP with all necessary components and connections, or interventions and improvement of the existing outdoor water network and sewerage network, connection of school facilities to the existing centralized water supply and sewage systems, for some particular schools (includes site assessment, design and technical documents, technical support to procurement, quality assurance and supervision):

| Sub-Package 1.1 A Rehabilitation of the existing WASH facilities within the building and adapting them to meet the needs of people with disabilities as well as construction of new facilities in a dedicated space within the building (by specific case). External works including installation of the WWTP with all necessary components and connections. |  |  |  |  |
| --- | --- | --- | --- | --- |
| 25 | TELENESTI | S. VADUL-LECA | Instituţia Publică Gimnaziul ”Pavel Bechet” |  |
| 28 | ORHEI | S. ZORILE | GIMNAZIUL ZORILE |  |
| 54 | SINGEREI | S. CHISCARENI | Instituţia Publică Liceul Teoretic ”Nicolae Casso” |  |
| 73 | REZINA | S. IGNATEI | Instituția Publică Liceul Teoretic "Ioan Sârbu" din s. Ignăţei |
| 80 | BRICENI | S. LARGA | Liceul Teoretic, Larga |  |
| 86 | FALESTI | S. GLINJENI | Gimnaziul M. Corlăteanu, Glinjeni |  |
| 112 | CAUSENI | S. COSCALIA | Instituția Publică Instituția de Învățământ „Gimnaziul Coşcalia” |  |
| Sub-Package 1.1 B Rehabilitation of the existing WASH facilities within the building and adapting them to meet the needs of people with disabilities as well as construction of new facilities in a dedicated space within the building (by specific case). External works including interventions and improvement of the existing outdoor water network and sewerage network and connection of school facilities to the existing centralized water supply and sewage systems. |  |  |  |  |
| 23 | TELENESTI | S. CRASNASENI | Instituţia Publică Gimnaziul Crăsnăşeni |  |
| 66 | CALARASI | S. TIBIRICA | Instituţia Publică Gimnaziul Ţibirica |
| 52 | CIMISLIA | S. GURA GALBENEI | Instituția Publică Liceul Teoretic "Hyperion", Gura Galbenei |  |
| 11 | BASARABEASCA | OR. BASARABEASCA | IP Gimnaziul "Ivan Bondarev" |
| 106 | ANENII NOI | S. SPEIA | Instituția Publică Gimnaziul Speia |
| 120 | HINCESTI | S. BOZIENI | IP Gimnaziul Bozieni |
| 74 | ANENII NOI | S. MERENI | Instituția Publică Şcoala primară grădiniță Mereni |
| 107 | CANTEMIR | S. TIGANCA | Instituţia Publică Gimnaziul "Ion Cojocaru" |

Sub-Package 1.2 Rehabilitation of the existing WASH facilities within the building and adapting them to meet the needs of people with disabilities as well as construction of new facilities in a dedicated space within the building (includes site assessment, design and technical documents, technical support to procurement, quality assurance and supervision):

| 34 | CHISINAU | S. BUBUIECI | Instituția Publică Liceul Teoretic „Toader Bubuiog”, Bubuieci |
| --- | --- | --- | --- |
| 38 | UTA GAGAUZIA | MUN. COMRAT | Instituția Publică Liceul Teoretic "Mihai Eminescu" din mun. Comrat |
| 47 | CAUSENI | OR. CAUSENI | Instituția de Învățământ Liceul Teoretic "Ion Creangă" |
| 59 | IALOVENI | S. HORESTI | Liceul Teoretic, Horeşti |
| 103 | ORHEI | S. GHETLOVA | INSTITUŢIA PUBLICĂ GIMNAZIUL GHETLOVA |
| 76 | TARACLIA | OR.TARACLIA | INSTITUŢIA PUBLICĂ GIMNAZIUL TARACLIA |

  - The contract will be signed with selected engineering firm for Package 1. The contract for Package 2 will be activated upon necessity and satisfactory completion of services under Package 1.

  - Potential Bidders shall visit the sites prior submitting their offers to get familiar with site conditions that may affect their Proposals. Potential Bidders are expected to make their own arrangements to visit the site and on their own expenses. UNICEF shall accept no excuse or claim whatever from the selected engineering firm for not knowing or being able to properly evaluate the site condition and requirements for the services to be carried out. Questions should be submitted in writing to UNICEF in accordance with instruction provided under the RFP.

  - All design drawings and technical documents developed for construction and/or renovation works implemented directly or indirectly by UNICEF shall be in line with the Organization’s commitments towards Accessible Buildings and achieving Climate Neutrality by 2020, as per PROCEDURE/DFAM/2020/001 on Eco-efficiency and Inclusive Access in UNICEF Premises and Operations, CF/EXD/2017-004 on Accessibility in UNICEF’s Programme-Relegated Construction, and Decision Memo: UNICEF Climate Neutral Strategy, 26 May 2015.

  - Policy documents mentioned at paragraph 3.6. and UNICEF Accessibility Technical Cards and Procedure on Eco-efficiency and Inclusive Access will be applied where possible, depending on the specific space availability and actual technical conditions in each location, and recommendations issued by National Agency of Public Health approved by Ministry of Education as guidance documents for renovation and building of washrooms in educational institutions in Moldova.

- EXPECTED DELIVERABLES

  - The table below describes in detail each required engineering service, including tasks and expected deliverables.

  - Deliverables shall be submitted to UNICEF in electronic format (drawings in AutoCAD and PDF) and hard copies printed in an appropriate scale.

Table 1: Services, Tasks and Deliverables

| # | Service Descriptions | Tasks | Deliverables |
| --- | --- | --- | --- |
| Package 1 |  |  |  |
| 1- | Site Assessment Evaluation of site characteristics and preparation of detailed analysis with recommendations for design and implementation. | 1.1 Assessment of existing buildings Verify structural integrity and functionality of existing construction, finish quality, accessibility level, accuracy of as-built drawings, and if not available, prepare architectural drawings of existing buildings. | Detailed report approved by UNICEF with site layout, collected data, as-built drawings, building(s) and site analysis and recommendations. |
|  |  | 1.2 Assessment of sites for evaluation of existing networks and determine suitability for construction of new wastewater treatment plant or additional outdoor networks required for connection of school facilities to centralized water and sewage systems Conduct site surveys (topographical, geotechnical and engineering); verify land legal status and construction laws. |  |
|  |  | Soil investigation Check the site topography for surface and subsurface exploration. Subsurface exploration involves soil sampling and laboratory tests of samples retrieved. | Detailed report approved by UNICEF on soil investigation. |
| 2- | Design and Technical Documents Development of construction technical documents, and obtaining necessary construction permits, if required. | 2.1 Conceptual design Produce design sketches that comply with site conditions, criteria, performance standards, greening and accessibility requirements; formulate and evaluate design options; develop conceptual design for the “passed-screening” option. | Feasibility report approved by UNICEF includes design criteria, options' analysis and conceptual design drawings. |
|  |  | 2.2 Architectural design Develop architectural design in 2 stages: a) Preliminary design based on approved conceptual design, and b) Detailed design with finish materials’ specifications. | Full set of architectural drawings with specifications, approved by UNICEF. |
|  |  | 2.3 Structural design Develop structural design in 2 stages: a) Preliminary design based on approved architectural design, and b) Detailed design with technical specifications and design analysis. | Full set of structural drawings, specifications, calculations and design analysis, approved by UNICEF. |
|  |  | 2.4 Building internal and external service design Develop design of indoor and outdoor utility systems: plumbing and sanitary facilities, heating and ventilation, electrical services, external water and sewage systems, in 2 stages: a) Preliminary design based on approved architectural design, and b) Detailed design with technical specifications and design analysis. | Full set of design drawings, specifications, calculations and design analysis, approved by UNICEF. |
|  |  | 2.5 Bid technical documents Prepare Bill of Quantities (BoQs) and confidential cost estimate; and compile all technical documents (design drawings, specifications and bill of quantities). | BoQs for repairs, rehabilitation and/or new construction approved by UNICEF. |
|  |  |  | Confidential cost estimates. |
|  |  | 2.6 Permitting and declaration Compile technical and administrative documents required for requesting permit and declaration, and obtain necessary construction permits and declaration for each construction work from Authority. | Original copy of permit(s) officially authorized by Authority. |
|  |  | 2.7 Author supervision Perform the author supervision during the construction phase. Ensure the compliance of the executed works with the provisions of the design documentation elaborated, verified and approved in the appropriate manner. | Documented visits, adjustments, and additions/supplements of the Design documentation if required |
| 3- | Technical Support to Procurement Assisting UNICEF in the solicitation process and the selection of qualified construction companies. | Support during the Bidding period Attend bidders’ conference with Potential Bidders; Provide answers and clarifications to their technical queries and questions during the preparation of bid period. | Report includes answers to all technical queries and questions of Potential Bidders during the bidding process. |
| Package 2 |  |  |  |
| 4- | Quality Assurance and Site Supervision Technical oversight of ongoing construction activities to ensure compliance with specifications and signed contract and provide advice to UNICEF on any potential risks related to timeline, budget and quality of works. | Quality assurance Undertake quality assurance and quality control plans and related procedures; review and approve contractor’s construction schedule, detailed designs, shop and as-built drawings; inspect material sources and materials’ tests. Site supervision Assist in project’s start-up; inspect and monitor time, progress, cost, quality and quantity of works and other agreed targets; approve workmanship and materials; certify payments and assist UNICEF in the control of variation orders; document project records that provide the necessary evidentiary and analyses in case of claims and disputes; ensure that works are executed in accordance with local Laws and regulations, national and international health and safety standards, quality standards and signed contract; liaise and co-ordinate with local authorities, if required; issue the Certificates of Partial, Substantial and Final Completion of works; prepare monthly progress reports and final narrative report; approve as-built drawings and Preventative Maintenance Manual. In case greening certification is pursued, engage with the Inclusive & Sustainable Operations team for guidance. | Reports approved by UNICEF based on site visits. |

- TIMEFRAME AND PAYMENT SCHEDULE

  - The timely completion of these engineering services is of utmost importance for UNICEF.

  - The duration required for completing Package 1 except “Author Supervision” and “Technical support for procurement” should be no later than two (3) months from date of signing the contract.

  - The duration required for completing Package 2 (if activated) will be linked to the construction contract timeframe but should not exceed 3-4 months.

  - The Defects Liability Period is [6] months counted as from the date of issuance of the Certificate of Substantial Completion.

  - UNICEF will issue interim and final payments upon satisfactory completion of each Deliverable.

Table 2: Timeframe and payment schedule

| # | Scope of deliverable | Payment distribution | Timeframe |
| --- | --- | --- | --- |
| Package 1 |  |  |  |
| 1 | After approval of UNICEF on completed deliverables of site assessment (Evaluation of site characteristics and preparation of detailed analysis with recommendations for design and implementation) | 20 % | two (2) weeks |
| 2 | After approval of UNICEF on completed deliverables of design and technical documents (Tasks 2.1 - 2.4 / Design criteria, options' analysis and conceptual design drawings; Full set of architectural drawings with specification; Complete set of structural drawings, specifications, calculations and design analysis; Full set of building service drawings, specifications) | 40 % | two (2) months |
| 3 | Final payment, after approval of the BoQs and permits (tasks 2.5 - 2.6) | 30 % | two (2) weeks |
| 4 | After providing technical Support during the Bidding period and signing the contract for Works with the Contractor. | 5 % | NA |
| 5 | After approval of UNICEF on completed deliverable of Author supervision (task 2.7) | 5 % | NA |
| Package 2 |  |  |  |
| 1 | After approval of UNICEF on report confirming the completion of mobilization and construction of site office with storage, and 2 water reservoirs with lid | 15% | NA |
| 2 | After approval of UNICEF on report confirming the completion of dismantling/demolition works | 15% |  |
| 3 | After approval of UNICEF on report confirming the completion of renovation/rehabilitation works | 15% |  |
|  | After approval of UNICEF on report confirming the completion and testing of all plumbing, water supply, sanitary, and electrical works | 15% |  |
| 4 | After approval of UNICEF on report confirming the completion of wash facilities | 15% |  |
| 6 | After approval of UNICEF on the report confirming the Substantial Completion and signing the Certificate of Substantial Completion | 15% |  |
| 7 | After approval of UNICEF on the report confirming the Final Completion and signing the Certificate of Final Completion | 10% | [6] months after Substantial Completion |

- KEY PERSONNEL

As a minimum the Engineering company must have employed the following stuff necessary to perform the assignment

  - Package 1:

- Project Manager (full-time) with 10-year experience in the domain.

- Architect with 6 - year experience in the domain.

- Structural/Civil Engineer with 5 - year experience in the domain.

- Electromechanical Engineer with 5-year experience in the domain.

- Water and Sanitation Engineer with 2-year experience in the domain.

- Heating, ventilation and air conditioning Engineer with 5-year experience in the domain.

- Topographer

- Interior designer with 5-year experience in the domain.

- BoQ specialist with 5-year experience in the domain

  - Package 2 :

- Project Manager with 8-year experience in the domain.

- Certified Technical Supervision Specialists (Rom equivalent: Responsabil Tehnic atestat) with 10 years relevant experience corresponding to the specific domain.

- ELIGIBILITY AND QUALIFICATIONS

  - The Potential Bidders are eligible to submit complete proposals for the services of Package 1 and Package 2 included in Section 4, and their submission will be taken into consideration in the proposal’s evaluation process.

  - The selected engineering firm is expected to assign or deploy adequate qualified staff to undertake the specific engineering services requested.

  - The Potential Bidder shall provide all the information and documentation requested in this section with its Proposal. Failure to submit the information below will disqualify the Potential Bidder.

  - Documents to be submitted in the Technical Proposal:

- The Potential Bidder must be registered as an engineering firm in Moldova. Technical Proposals shall include copies of original documents defining the constitution or legal status of the company, place of registration, and principal place of business; written power of attorney of the signatory of the nominated person to commit the contract.

- Copy of curriculum vitae (Maximum two (2) pages) of key personnel requested in Section 6 involved in providing the relevant service. UNICEF may conduct reference checks on the key personnel during the evaluation process.

- Copies of the technical qualification certificates

- Reports on the financial standing of the Potential Bidder.

  - The Potential Bidder must provide sufficient information in their proposal to demonstrate compliance with the requirements defined by UNICEF. The forms listed below contains the eligibility and minimum qualifying criteria that UNICEF will use to evaluate proposal for the award of the contract.

- Information to be submitted in the Technical Proposal (ANNEX C):

- Form 1: Technical Proposal Submission

- Form 2: Technical Proposal Letter

- Form 3: Potential Bidder’s General Information

- Form 4: Potential Bidder’s Contact Details

- Form 5: List of Completed Similar Services Undertaken the Last 3 Years

- Form 6: List of Similar Services in Hand

- Form 7: Proposed Methodology for the Implementation

- Form 8: Proposed Planning (Gantt Chart) for the Implementation

- Form 9: List of Proposed Key Personnel

- Form 10: CV of the Proposed Team

- Form 11: List of Office Equipment, Engineering Instruments and Design Software

- Form 12: Potential Bidder’s Financial Information/ Adequacy of Working Capital

- Form 13: Summary of Service Values Undertaken the last 3 Years

- Form 14: List of Current Litigations

- Information to be submitted in the Price Proposal (ANNEX D):

- Form 15: Price Proposal Letter

- Form 16: Price Proposal Submission

  - Errors in the Proposals

- In the event of any discrepancy between the copies of the Proposals submitted as hard copies, the original shall govern. The original and each copy of the Technical and Price Proposals shall be prepared in indelible ink and shall be signed by the authorized Firm’s representative.

- The Proposal shall contain no interlineations or overwriting except as necessary to correct errors made by the Bidders themselves. Any such correction shall be initialled by the person or persons signing the Proposal.

  - The following criteria will be considered for selection of Potential Bidders for the award of the contract:

- The capacity of the engineering firm to manage multiple assignments at the same geographical locations of this project.

- The engineering firm has demonstrable capacity (staff, equipment, logistics, finance) in similar types of assignment.

- The Potential Bidder must have wide range of experience and technical expertise in the field of construction engineering consultancy (at least 5 years).

- The Potential Bidder must be well informed of the construction engineering context of Moldova and is very familiar with country national construction norms and building legislation.

- The working experience with international and UN Organizations will be preferable.

- EVALUATION PROCESS AND METHOD

  - Following closure of the RFP, the Proposals will be evaluated by the evaluation team in 3 steps following the Proposal Evaluation Process stated in the RFP document. The evaluation will be restricted to the contents of the Proposals and the reference checks.

  - The technical merits of each Technical Proposal will be evaluated using the rating system in Table 3 (below) on the basis of the Proposal Evaluation Approach stated in the RFP document.

Table 3: Technical Evaluation Criteria

| CRITERIA | MAXIMUM POINTS |
| --- | --- |
| TECHNICAL EVALUATION | 70 |
| - Firm’s Profile - Five (5) years as an engineering firm providing similar services (Water and sanitation, architectural and civil engineering). - Proven experience in the country and similar services undertaken in the last 3 years; | 10 |
| - Firm’s Experience - Completed services of similar nature completed in past three (3) years with reference, as per Form 5; - Type of clients to whom the services were provided (Government, private sector, UN Organizations, others); | 20 |
| - Proposed Methodology and Planning - Proposed work plan (Gantt Chart) for implementing per Packages. - Proposed methodology and recourses allocation per packages | 10 |
| - Resources (key personnel and equipment) - Key personnel proposed to provide the services, including CVs, years of experience in similar services (proof required), education degree certificate (as requested, under 6. Key personnel); - List of essential support staff; - List of office equipment, engineering instruments and design software owned by the firm. - Size and structure of the firm and the capacity of the engineering firm to manage multiple assignments. | 25 |
| - Financial Capacity - Financial reports for the last 2 years (2022 and 2023) | 5 |

# ANNEX C: TECHNICAL PROPOSAL FORMS

The following Forms and information there within are considered an integral part of this submission and must be provided for the Proposal to be considered. The information should be provided according to the sample format.

Form 1: Technical Proposal Submission

This PROPOSAL FORM must be completed, signed and returned to UNICEF. Proposal must be made in accordance with the instructions contained in this Request for Proposal.

INFORMATION

Any request for information concerning this invitation, must be forwarded in writing by email or by fax, to the person who prepared this document, with specific reference to the RFP number.

DECLARATION

The undersigned, having read the Terms of Reference, the UNICEF Contract for Engineering Services, and RFP# [LRPS-2024-…………….] set out in the attached document, hereby offers to supply the services specified in Terms of Reference at the price or prices quoted in the Schedule of Prices, in accordance with the specifications stated and subject to the Terms and Conditions set out or specified in the RFP# [LRPS-2024-……………………….]

Name of authorized representative: 		_______________________________________

Title:						_______________________________________

Signature:					_______________________________________

Date:						_______________________________________

Supplier Name:				_______________________________________

Postal Address:				_______________________________________

Telephone No.:				_______________________________________

Fax No.:					_______________________________________

Email Address:				_______________________________________

Validity of Offer (not less than 90 days):	_______________________________________

Currency of Offer:				_______________________________________

Form 2: Technical Proposal Letter

Date: ___________

To: 	UNICEF Moldova, 131, 31 August 1989, MD-2012, Chisinau, Moldova

Dear Madam/Sir,

We, the undersigned, offer to provide engineering services in [country name] in accordance with your Request for Proposal RFP# [LRPS-2024-…………….] dated [e.g., July 2024] and our Proposal dated [---------------]. We are hereby submitting our Proposal, which includes this Technical Proposal and a Price Proposal sealed under separate envelopes.

If negotiations are held during the period of validity of the Proposal, we undertake to negotiate based on the proposed staff. Our Proposal is binding upon us and subject to the modifications resulting from Contract negotiations.

We understand that you are not bound to accept any Proposal you receive.

Yours sincerely,

Authorized Signature:

Name and Title of Signatory:

Name of Construction Company

Address:

Form 3: Potential Bidder’s General Information

| Potential Bidder General Information |  |  |
| --- | --- | --- |
| Description | Information | Remarks |
|  | (to be filled by the Potential Bidder) |  |
| Registration number |  |  |
| Grade |  |  |
| Specialty |  |  |
| Expiry Date |  |  |
| Legal Status |  | Provide certified copies of Registration |
| Written power of attorney of the signatory to the Bid | Provide original or certified copy of the power of attorney attested by a Notary |  |
| VAT Registration Nr. |  |  |
| UNGM Registration Nr. |  |  |

Form 4: Potential Bidder’s Contact Details

| Name and Title of Contact Person |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Address of Contact Person |  |  |  |  |  |
| Telephone/Cell number of Contact Person |  |  |  |  |  |
| Email of Contact Person |  |  |  |  |  |

Form 5: List of Completed Similar Services Undertaken the Last 3 Years

Please provide copies of signed Contracts and Certificates of final completion for each completed service.

| Completed Services |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Employer name & contact details |  | Description of Services | Start date | End date | Value |

Form 6: List of Similar Services in Hand

Please provide copies of signed Contracts for each service in hand.

| Completed Services |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Employer name & contact details |  | Description of Services | Start date | Expected end date | Value |

### Form 7: Proposed Methodology

Please provide methodology proposed by the Potential Bidder, the approach suggested for implementing the required engineering services, the plan for quality assurance, etc.

### Form 8: Proposed Planning

Please provide detailed planning (Gantt Chart) proposed by the Potential Bidder for implementing.

### Form 9: List of Proposed Key Personnel

Qualifications and experience of key management and technical personnel proposed for the required services. Signed CVs (Max. two (2) pages) and education degree certificate of all proposed key staff must accompany the submission, and it should be noted that substitution of staff during Project implementation shall be subject to the approval of UNICEF. (Key Personnel of all sub-Contractors must also be listed along with the name of the sub-Contracting Companies). A detailed organization chart of the company, including the location and staffing of existing offices must also be attached to the offer.

| Management Key Staff |  |  |
| --- | --- | --- |
| - Key Professionals for Design Stage |  |  |
| Name | Position | Task |
| - Key Professionals for Site Supervision Stage |  |  |
| Name | Position | Task |
| - Support Staff |  |  |
| Name | Position | Task |

### Form 10: CV of the Proposed Team

CV for each category of the services bidding for.

| Position Title and No. | [e.g., PROJECT MANAGER] |
| --- | --- |
| Name of Expert: | [Insert full name] |
| Date of Birth: | [day/month/year] |
| Country of Citizenship/Residence |  |

Education: List in reverse order starting with highest degree obtained up to Graduate Degree, the university/ institution or other specialized education, giving the following details:

| S. No. | Degree/Diploma/Certificate obtained | Name of University/ Institution | Duration (mm-yyyy) |  |
| --- | --- | --- | --- | --- |
|  |  |  | From | To |

Employment record relevant to the services: Starting with present position, list in reverse order. Please

provide dates, name of employing organization, titles of positions held, types of activities performed and

location of the service, and contact information of previous clients and employing organization(s) who

can be contacted for references. Past employment that is not relevant to the service does not need to be included.

| Period | Employing organization and your title/position. | Contact information for references | Summary of activities performed relevant to the Assignment |
| --- | --- | --- | --- |
| [e.g., May 2005-present] | [e.g., Ministry of ……, staff/advisor/consultant to… | Tel………/e-mail……; Mr. xxxxx, [deputy director] |  |

Membership in Professional Associations:

1.

2.

List of papers published in your name in peer reviewed/national/international journals:

1.

2.

Proficiency in Language Skills (indicate only languages in which you can work i.e. read, write, speak):

| Languages | Read |  | Write |  | Speak |  | Understand |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Not |  | Not |  | Not |  | Not |
|  | Easily | Easily | Easily | Easily | Easily | Easily | Easily | Easily |
| English |  |  |  |  |  |  |  |  |
| Bengali |  |  |  |  |  |  |  |  |
| Others (specify) |  |  |  |  |  |  |  |  |

Expert’s contact information: (e-mail …………………., phone……………)

### Form 11: List of Office Equipment, Engineering Instruments and Design Software

| Office Equipment, Engineering Instruments and Design Software |  |  |  |
| --- | --- | --- | --- |
| - Office Equipment |  |  |  |
| Description | Quantity | Brand, Model, Specifications |  |
| - Engineering Instruments |  |  |  |
| Description | Quantity | Brand, Model, Specifications | Owned/Rented |
| - Design Software |  |  |  |
| Name | Version | Utilization |  |

Form 12: Potential Bidder’s Financial Information/ Adequacy of Working Capital

IMPORTANT: Please provide attached copies of Audited Financial Reports for the last three (2) years.

| Adequacy of Working Capital |  |  |  |
| --- | --- | --- | --- |
| Source of credit line |  | Amount | Remarks |
|  |  |  | Provide documentary evidence |
| Total: |  |  |  |

Form 13: Summary of Service Values Undertaken the Last 3 Years

| Service Values for the Last 3 Years |  |  |  |  |
| --- | --- | --- | --- | --- |
| Employer name & contact details |  | Description of Services | Duration | Value |
| Total: |  |  |  |  |

Form 14: List of Current Litigations

Please provide information on any current litigation in which the Firm(s) is involved.

| Other Party(ies) | Cause of Dispute | Amount Involved |
| --- | --- | --- |

# ANNEX D: PRICE PROPOSAL FORMS

Form 15: Price Proposal Letter

Date: ___________

To: 	UNICEF Moldova, 131, 31 August 1989, MD-2012, Chisinau, Moldova

Dear Madam/Sir,

We, the undersigned, offer to provide engineering services in [country name], as specified in the Annex B, following your Request for Proposal RFP# [LRPS-2024-…………….] dated [e.g., July 2024] and our Technical Proposal in the Annex C.

Our attached Price Proposal is for the sum of (---------------------------------------------------------------------------------------------------------------------------amount in figures and words).  This amount is inclusive of all taxes payable under the applicable law.

Our Price Proposal shall be binding on us subject to the modifications resulting from Contract negotiations, up to the expiration of the validity of the Proposal.

We understand that you are not bound to accept any Proposal you receive.

Yours sincerely,

Authorized Signature:

Name and Title of Signatory:

Name of Construction Company

Address:

Form 16: Price Proposal Submission

Please fill the summary price offer template below and include a breakdown of the costs per school and the Personnel services cost table

Tab 1, Price offer summary

| Service description | Price, MDL |
| --- | --- |
| Package 1 |  |
| Sub-package 1.1 |  |
| 1 Site Assessment |  |
| 2 Design and Technical Documents |  |
| 3 Technical Support to Procurement |  |
| Total Sub-package 1.1 |  |
| Sub-package 1.2 |  |
| 1 Site Assessment |  |
| 2 Design and Technical Documents |  |
| 3 Technical Support to Procurement |  |
| Total Sub-package 1.2 |  |
| Total Package 1 |  |
| Package 2 |  |
| Sub-package 2.1 |  |
| 4 Quality Assurance and Site Supervision |  |
| total Sub-package 2.1 |  |
| Sub-package 2.2 |  |
| 4 Quality Assurance and Site Supervision |  |
| total Sub-package 2.2 |  |
| Total Package 2 |  |
| Grand Total |  |

Tab 2 Breakdown of the costs per school

| No | School name | Service description |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Package 1 |  |  |  | Package 2 |  |
|  |  | Site Assessment | Design and Technical Documents | Technical Support to Procurement | Quality Assurance and Site Supervision |  |
|  | Sub-package 1.1 |  |  |  |  |  |
| 1 | School name |  |  |  |  |  |
| 2 |  |  |  |  |  |  |
| ….. |  |  |  |  |  |  |
|  | Sub-package 1.2 |  |  |  |  |  |
| 1 | School name |  |  |  |  |  |
| 2 |  |  |  |  |  |  |
| ….. |  |  |  |  |  |  |

Tab 3 Breakdown of the costs using the Personnel services.

As a minimum the Engineering company must have the following personnel necessary to perform the assignment

This breakdown will exclusivity be used for determining remuneration for additional services provided under this assignment.

| Service Description | Unit | Unit Price (Fully loaded) |
| --- | --- | --- |
| - Project Manager | Per Day |  |
| - Architect | Per Day |  |
| - Structural/Civil Engineer | Per Day |  |
| - Electromechanical Engineer | Per Day |  |
| - Water and Sanitation Engineer | Per Day |  |
| - Heating, ventilation and air conditioning Engineer | Per Day |  |
| - Topographer | Per Day |  |
| - Interior designer | Per Day |  |
| - BoQ specialist | Per Day |  |
| - Site Supervision during execution of works |  |  |
| - Project Manager (full-time) | Per Day |  |
| - Technical supervisor (Responsabil Tehnic atestat) | Per Day |  |
| - Site visit report (all costs included) | Per visit |  |
| - Monthly monitoring and reporting (all costs included) | Per month |  |

UNICEF will assume that the bidders will have factored in its offer all causes that may have an influence on the prices. Therefore, the costs indicated above should include all costs and benefits related to labor, including but not limited to:

- Head office overhead charges and reporting;

- Travel expenses to remote sites;

- Time lost due to inclement weather;

- Bonuses and all other incentive payments;

- Contribution to training levy and all statuary contributions;

- Contributions for annual and public holidays;

- Fares and time allowances for traveling;

- Safety and welfare facilities;

- Workmen's compensation and third-party liability insurance’s, sick pay or insurance in respect thereof;

- Obligations for redundancy payments;

- Engineering tool and instrument allowance;

- Use, repair and up keeping of engineering tools and instruments;

- Protective clothing and safety personnel protection;

# ANNEX E: TECHNICAL SPECIFICATIONS

GENERAL TASKS

UNICEF is seeking proposals from qualified engineering/design firms to provide services for the design of WASH (Water, Sanitation, and Hygiene) sanitary groups in schools. The objective is to improve sanitation facilities to ensure the well-being and hygiene of students and staff.

SCOPE OF WORK

Design Company will prepare the design and technical documentation for the following tasks:

- Rehabilitation of the existing WASH facilities within the building and adapting them to meet the need of people with disabilities, as well, by specific case, will be analyzed the possibility of creation of new sanitary groups in a dedicated space within the building.

- Construction of the external sewage system, including the main collector, wastewater treatment plant (WWTP) and all necessary connections and components.

- Design and oversee the connection of school facilities to the existing centralized water supply and sewage systems, including the construction of all necessary external networks.

The Design Company is encouraged to visit the proposed sites, in order to familiarize themselves with the current conditions and identify suitable solutions for improvement.

Design Company shall undertake the following tasks:

- Site Assessment and Preliminary Data Collection:

- Conduct a technical assessment of the existing school buildings, including an evaluation of structural integrity, functionality, finish quality, accessibility level, and other relevant investigations as appropriate.

- Conduct the site assessment to identify the location for the new constructions, including the installation of the WWTP and all necessary components, or construction of all necessary external networks required for connection of school facilities to the existing centralized water supply and sewage systems. Perform the topographic survey and geotechnical analysis.

- Obtain necessary technical conditions for utilities connections (including preparation of necessary supporting documents, connection schemes and routes, load, and utilities consumption requirements calculations) if required.

- Design and Compartments:

- Prepare the preliminary Design for internal works including WASH facilities in existing spaces of the school building, and for those intended to accommodate the additional facilities ensuring it meets all necessary requirements and standards.

- Prepare the preliminary Design for the external works including water and sewage system, WWTP and all necessary connections and components, interventions and improvement of the existing outdoor networks, connection of school facilities to the existing centralized water supply and sewage systems or other in accordance with the urban certificate and appropriate norms and regulations.

- Prepare the final Design and technical documentation covering all compartments: Architecture, Constructive/Structural Solutions (ACS), Electric Lighting/Power Equipment (EL/FPE), Internal and External Water Supply and Sewage System (WSSW), Wastewater treatment plant (WWTP), Heating and Ventilation (HV), Organization of Construction Works (OCW), Cost Estimation and Bill of Quantities (CE/BoQ).

- Obtain necessary technical approvals and coordination of the design documentation from all relevant institutions, in accordance with the provisions of the local regulations.

- The final Design documentation will be verified by authorized experts and its conformity will be confirmed by issuing the appropriate verification report.

- Estimation and Cost Verification:

- Calculate the Bill of Quantities considering all requirements of the beneficiary (School Administration, UNICEF representatives) regarding materials, capacity, dimensions, etc.

- The CE/BoQ should be calculated considering the probability of unforeseen or hidden works that may be discovered after the demolition or dismantling works are carried out.

- In accordance with local regulations, the CE/BoQ is also subject to verification and issuance of verification report, as well as for Design documentation.

- Additional requirements:

- Provide deliverables in three copies on paper and in electronic format (DWG, PDF, WORD) to both UNICEF and the beneficiary. Ensure that all formats are easily accessible and compatible for review and distribution.

- Maintain open and timely communication with UNICEF, the school administration, and the contractor throughout the project lifecycle. Respond promptly to inquiries and provide regular updates on project progress, milestones, and any issues encountered.

- Ensure the quality and accuracy of all deliverables and consultancy services provided. Conduct thorough reviews and quality checks to uphold professional standards and meet the expectations of both UNICEF and the beneficiary.

- Other Specific Considerations:

- The number of sanitary groups per school should be based on the current number of students, as provided by the school administration.

- The improvement of school WASH facilities must include such components like plumbing and sanitary facilities, water supply system, sewerage system, electrical system, heating and ventilation system, flooring, walls, and ceilings, handwashing facilities, accessibility features, waste management, aesthetic, and functional improvements.

- In case the school does not have a hot water network, the design company should take into consideration installation of water heaters and local hot water network to ensure the access to hot water at the handwashing facilities.

- Ensure that all sanitary groups are equipped with mirrors, paper holders, soap dispensers and hand dryers.

- Ensure that any reconstruction or interventions required for the sanitary groups are included in the technical expertise and design documentation. Major interventions beyond the scope should be discussed with the UNICEF and school administration.

- Environmental factors should be considered, such as terrain, drainage, and proximity to existing infrastructure, in determining the optimal placement of sanitary facilities.

- All design aspects and equipment choices will be preliminary coordinated with the school administration and UNICEF representatives to ensure functionality and compliance with standards.

- All these requirements, including but not limited to those related to the functionality of the designed sanitary groups and the installation of equipment such as water heaters and electric dryers, will be coordinated closely with the school administration and UNICEF representatives. Their input and approval will be sought to ensure that the final design meets the needs and standards required for the project's success.

- Design standards and norms

- The design works are to be carried out in accordance with local legislation as well as with the norms and standards in force.

- Whenever reference is made in the design to specific standards and codes that materials, installations, and other goods to be provided must comply with, as well as the works to be performed or tested, the provision of the latest editions or current revisions of the regulations and practical codes in force shall apply, unless expressly stated otherwise in the contract.

- In order to ensure fairness and accessibility to all products on the market, the specifications outlined in the design documentation must be generic and applicable to various solutions in the WASH design. Specific product endorsements or recommendations are not acceptable. The design should focus on technical parameters that accommodate different suppliers and technologies within the field.

- The design requirements must ensure that the sanitary groups in all schools are accessible to persons with reduced mobility as per national standard requirements, UNICEF Technical Cards and Climate, Energy, Environment and Disaster Risk Reduction (CEED).

PARTICULAR DATA FOR SELECTED LOCATION

The data and assessments provided in this chapter are intended to familiarize the engineering firm with the site conditions and school requirements. While every effort has been made to ensure the accuracy and completeness of this information, engineering firms are advised not to rely solely on it when preparing their offers. It is the responsibility of the engineering firms to conduct their own independent assessments and verifications to ensure the accuracy of their proposals. The information provided herein is for reference purposes only and should be used as a guide to assist in understanding the general project scope and requirements.

It should be considered as well that the assessment was performed a few months ago, and there may be changes or updates to the site conditions since then. Therefore, companies are encouraged to conduct their own site assessments and verify all relevant information before submitting their offers.

Thus, the engineering firm’s offer should be based on their own independent analysis and assessment of the project requirements and site conditions.

R.Telenești, s.Crăsnășeni, ID 23

The Crăsnășeni Gymnasium is designed in 3 levels. The building was put into operation 1987 and was initially designed to serve as a school. The institution is divided into two blocks separated for primary and middle school. The age of the students ranges from 7 to 16 years old. The school operates on a single-shift schedule.

The indoor sanitary facilities are non-functional due to deteriorated water and sewerage systems, electrical issues, inadequate ventilation, and outdated flooring, walls, and ceilings. Students and staff are using outdoor sanitary blocks located at a distance of 100 m from school.

The institution is connected to the centralized water supply system, and water is delivered to the building. There is a total of 5 functional points of distribution of drinking water. The water from distribution points is potable.

Wastewater is discharged in a cesspool. A wastewater treatment plant was built in 2023 but was not put into operation due to non-functional sanitary groups.

Table 15 Demographics of school r.Telenești, s.Crăsnășeni

| Boys | 64 |
| --- | --- |
| Girls | 55 |
| Childrens with limited mobility | 0 |
| Total Students | 119 |
| Teaching Staff | 15 |
| Technical Staff | 12 |
| Total Staff | 27 |

Particular recommendations to take into consideration for selected location (but not limited to these):

- Develop the detailed design for rehabilitation of the indoor WASH facilities on levels 1, 2, and 3. Ensure the connection of the rehabilitated school wash facilities with the new built WWTP.

- Design should also include the accommodation of sanitary groups for persons with limited mobility.

- The design should address any structural and functional issues present in the existing sanitary facilities and handwash facilities including renewing flooring, walls, and ceilings, and ensuring that all elements meet current health, safety, and accessibility standards. Considerations should also include upgrading plumbing and sanitary facilities, water supply system, sewerage systems, renovating fixtures and fittings, improving heating and ventilation, electrical system, installation of water heaters, handwashing facilities, waste management, aesthetic, and functional improvements, ensuring accessibility for persons with disabilities, and adhering to relevant building codes and regulations.

- Additionally, prioritize the use of sustainable and durable materials to enhance the longevity and efficiency of the rehabilitated sanitary groups.

| Block C, al (II) GTS Level 1 right | Block C, al (II) GTS Level 1 right |  |  |
| --- | --- | --- | --- |
| Block C, al (I) GTS Level 1 right | Block C, al (I) GTS Level 1 right |  |  |
| Block C, GTS Level 1 left | Block C, GTS Level 1 left |  |  |
| Block C, GTS Level 2 left | Block C, GTS Level 2 left |  |  |
| Block C, GTS Level 2 right | Block C, GTS Level 2 right |  |  |
| Block C, GTS Level 3 right | Block C, GTS Level 3 right |  |  |
| Block C, GTS Level 3 right | Block C, GTS Level 3 right |  |  |
| Block C, GTS Level 3 left | Block C, GTS Level 3 left |  |  |
| Block C, GTS Level 3 left | Block C, GTS Level 3 left |  |  |
| GTS kitchen staff | Washbasins – canteen access |  |  |
| GTS girls locker room | Vestiary shower girls |  |  |
| GTS boys locker room | Vestiary shower boys |  |  |
| Block B GTS Level 2 | Block B GTS Level 2 |  |  |
| Sanitary group, block C, floor 1 (left side I) |  | Sanitary group, block C, floor 1 (right side I) |
| Sanitary group, block C, floor 1 (right side II) |  | Sanitary group, block C, floor 2 (left side) |
| Sanitary group, block C, floor 2 (right side) |  | Sanitary group, block C, floor 3 (left side) |
| Sanitary group, block C, floor 3 (right side) |  | Kitchen toilet |

| Photo 69 Female locker room | Photo 70 Male locker room |
| --- | --- |
| Photo 71 Sanitary group, block B, floor 2 |  |

R. Telenești, s. Vadul-Leca, ID 25

The gymnasium represents one level block. No renovation works have been initiated for WASH facilities in the last period. Water source is the local centralized system. There are no water filters in the institution and the drinking water is provided bottles in the hall and from 4 sinks near canteen. Wastewater is discharged into a cesspit/tank built in 2016 on the school premises, being evacuated once a year. The locality does not have centralized sewerage system or treatment plant. In 2023, the design documentation for construction of the sanitary groups was initiated. However, the works did not continue due to lack of funds.

The institution does not have sanitary groups built inside it and does not have a place specially designed for it. As a solution it is proposed to use the space of the class #2 room for the design and construction of the sanitary groups.

Table 5 Demographics of school r. Telenești s. Vadul-Leca

| Boys | 63 (34 class 1-4) |
| --- | --- |
| Girls | 52 (20 boys grade 1-4) |
| Pupils with disabilities | 2 children with locomotor problems, home training because there is no stroller access in the institution |
| Total pupils | 115 |
| Teaching staff | 15 |
| Other staff | 12 |
| Total Staff | 27 |

Particular recommendations to take into consideration for selected location (but not limited to these):

- Develop the detailed design of the wastewater treatment plant (WWTP) and connection to building sewerage system to ensure efficient treatment of wastewater from the sanitary facilities. Including connection of wastewater and water pipes for constructed sanitary groups.

- Develop the detailed design for the construction of sanitary groups for boys and girls by repurposing the "Class II" classroom. Additionally, it is proposed to convert part of the hall into a shared sanitary block for people with limited mobility and staff. The improvement of school indoor WASH facilities must include such components like water supply system, sanitation system, plumbing and sewerage system, electrical system, ventilation system, flooring, walls, and ceilings, handwashing facilities, accessibility features, waste management, aesthetic, and functional improvements.

- The design should include measures for waterproofing the foundation of the future sanitary groups, considering that the external soil level is higher than the classroom floor level.

- The design should address any structural and functional issues present in the existing sanitary facilities and handwash facilities including renewing flooring, walls, and ceilings, and ensuring that all elements meet current health, safety, and accessibility standards. Considerations should also include upgrading plumbing and sanitary facilities, water supply system, sewerage systems, renovating fixtures and fittings, improving heating and ventilation, electrical system, installation of water heaters, handwashing facilities, waste management, aesthetic, and functional improvements, ensuring accessibility for persons with disabilities, and adhering to relevant building codes and regulations.

- Additionally, prioritize the use of sustainable and durable materials to enhance the longevity and efficiency of the rehabilitated sanitary groups.

Canteen access

Access corridor to the toilets to be built

Changing the destination of the classroom into technical-sanitary groups – elaboration of execution project, water network, sewerage, ventilation and lighting

| Existing space | Proposed sanitary block |
| --- | --- |

R. Orhei, s. Zorile ID 28

The school building was commissioned in 1984, with sanitary groups planned for the first and second floors. However, due to the lack of centralized sewage system in the locality, these facilities have never been used. No renovation works have been initiated in the sanitary facilities since their commissioning.

Water supply is sourced from a centralized system, meeting requirements for drinking water. There are no water filtration facilities within the institution, and the only water distribution point is in the institution's corridor within the cafeteria, with hot water available.

At the moment, students, teachers, and technical staff use the outdoor latrines. There are no showers or toilets for the sports hall. According to the standards for a middle school institution, special spaces for sanitary facilities were planned on each floor and within the sports hall. While there is a toilet built within the institution, it cannot be used due to the lack of sewerage system. Similarly, there are no other indoor sanitary facilities within the school, although space is allocated for them on the first and second-floor corridors, as well as near the sports hall, where a special area for showers and toilets is planned. At the time of the visit, only outdoor latrines are used.

Wastewater from the cafeteria is discharged into an old cesspool that is not cleaned regularly.

Table 43 Demographics of school, r. Orhei, s. Zorile

| Boys | 63 |
| --- | --- |
| Girls | 47 |
| Students with limited mobility | 2 |
| Total Students | 110 |
| Teaching staff | 15 |
| Technical staff | 8 |
| Total Staff | 23 |

Particular recommendations to take into consideration for selected location (but not limited to these):

- Develop the detailed design of the wastewater treatment plant (WWTP) and connection to building sewerage system to ensure efficient treatment of wastewater from the sanitary facilities. Including connection of wastewater and water network for constructed sanitary groups.

- Develop the detailed design for renovation and construction of sanitary groups, for children (boys and girls), technical staff, and teaching staff, as well as for those with limited mobility. Renovation of sanitary facilities and shower for the sports hall. Technical staff from kitchen need construction of sanitary facilities.

- The design should address any structural and functional issues present in the existing sanitary facilities and handwash facilities including renewing flooring, walls, and ceilings, and ensuring that all elements meet current health, safety, and accessibility standards. Considerations should also include upgrading plumbing and sanitary facilities, water supply system, sewerage systems, renovating fixtures and fittings, improving heating and ventilation, electrical system, installation of water heaters, handwashing facilities, waste management, aesthetic, and functional improvements, ensuring accessibility for persons with disabilities, and adhering to relevant building codes and regulations.

- Additionally, prioritize the use of sustainable and durable materials to enhance the longevity and efficiency of the rehabilitated sanitary groups.

| Canteen access, it is necessary to repair the ceiling, floor, tile, changed washbasins and sewage system | Canteen access, it is necessary to repair the ceiling, floor, tile, changed washbasins and sewage system |
| --- | --- |
| 1st floor, change from common hallway to GTS for girls, children with SEN needs and staff | 1st floor, change from common hallway to GTS for girls, children with SEN needs and staff |
| 2nd floor, change from common space to GTS for boys | 2nd floor, change from common space to GTS for boys |
| GTS inside the canteen | GTS inside the canteen |
| Teaching and technical staff, access from the corridor | Teaching and technical staff, access from the corridor |
| Repaired 2016, cannot be used due to lack of sewage system, need ventilation, door replacement | Repaired 2016, cannot be used due to lack of sewage system, need ventilation, door replacement |
| Boys gym | Boys gym |
| Girls gym | Girls gym |

R. Cimișlia, s.Gura Galbenei, ID 52

The school consists of a four-block complex. Block A is designated for the middle and high school classes, while block C for the primary classes.

The sanitary groups on level 1, block A and block C were recently rehabilitated. In the renovated sanitary groups as well as in those to be renovated, there is no ventilation system. In addition, the renovated sanitary groups in Blocks A and C do not comply with accessibility standards for persons with reduced mobility and fail to provide the required level of privacy.

The kitchen and block A are connected to the wastewater treatment plant, while block C is connected to a tank that is emptied periodically.

There is a recently renovated sanitary block provided for the kitchen staff. There is no hot water available at any washbasins. The water is potable, tested at the beginning of the academic year. Water filters are installed at the flow evidence point. There is an additional construction outside the institution intended as a sanitary group.

Table 16 Demographics of school r.Cimișlia, s.Gura Galbenă

| Boys | 140 |
| --- | --- |
| Girls | 276 |
| Pupils with disabilities | 0 |
| Total pupils | 416 |
| Teaching staff | 32 |
| Other staff | 26 |
| Total Staff | 58 |

Particular recommendations to take into consideration for selected location (but not limited to these):

- Develop the detailed design for connection of Block C to the existing WWTP (approximately distance 120 meters).

- Develop the detailed design for increasing the number of wash facilities by rehabilitation/construction of sanitary groups in the space identified by the school administration. Ensure seamless connectivity with the WWTP to facilitate efficient management of wastewater from the sanitary facilities (2 sanitary groups at 3rd floor in the wing for teenagers for girls and boys), (1 sanitary group for girls at 2nd floor for teenager’s wing), (1 sanitary group for 2nd floor in the primary classes wing for girls & boys).

- The design should also include construction of sanitary groups for persons with limited mobility.

- The design should address any structural and functional issues present in the existing sanitary facilities and handwash facilities including renewing flooring, walls, and ceilings, and ensuring that all elements meet current health, safety, and accessibility standards. Considerations should also include upgrading plumbing and sanitary facilities, water supply system, sewerage systems, renovating fixtures and fittings, improving heating and ventilation, electrical system, installation of water heaters, handwashing facilities, waste management, aesthetic, and functional improvements, ensuring accessibility for persons with disabilities, and adhering to relevant building codes and regulations.

- Additionally, prioritize the use of sustainable and durable materials to enhance the longevity and efficiency of the rehabilitated sanitary groups.

| GTS boys, level 1, block A. GTS girls, level 1, block C |  |  |  |
| --- | --- | --- | --- |
| GTS girls, level 1, block A. |  |  |  |
| GTS boys, level 1, block C. |  |  |  |
| Camera for boys GTS, level 2, block A. |  |  |  |
| Camera for GTS girls, level 2, block A. |  |  |  |
| Camera for boys GTS, level 3, block A. |  |  |  |
| Camera for GTS girls, level 3, block A. |  |  |  |
| Space for GTS girls/boys, level 2, block C. |  |  |  |
| space for GTS girls/boys, level 2, block C. |  |  |  |
| Photo 72 female sanitary group, floor 2 |  | Photo 73 female sanitary group, floor 2 |
| male/female sanitary group, floor 2, block C |  | GTS boys plans, level 2, block A |

R. Sîngerei, s. Chișcăreni, ID 54

The school building represents a 3-storey block built in 1960. The school operates in a single shift, the total number of students being 376, of which girls 193, boys 183. In 2007 the water supply network was repaired and in 2019 the sewerage system was renovated by building the cesspit/tank type reservoir.

In 2012 sanitary groups were built inside the building. In total there are 11 toilet cubicles, of which there are 9 functional.

The institution is connected to a centralized water supply system but has no connection to centralized sewerage system, wastewater and waste being stored in the cesspit/tank and emptied once per year. Currently functional toilets are in satisfactory condition, but require some improvement, namely: Installation of soap dispensers, paper towel holders, hand dryers, replacement of broken faucets and water taps.

Table 8 Demographics of school, r. Sîngerei, s. Chișcăreni

| Boys | 183 |
| --- | --- |
| Girls | 193 |
| Pupils with disabilities | 0 |
| Total pupils | 376 |
| Teaching staff | 31 |
| Other staff | 21 |
| Total Staff | 52 |

Particular recommendations to take into consideration for selected location (but not limited to these):

- Develop the detailed design of the wastewater treatment plant (WWTP) and connection to building sewerage system to ensure efficient treatment of wastewater from the sanitary facilities. Including connection of wastewater and water pipes for constructed sanitary groups.

- Develop the detailed design for renovation of non-functional toilets and construction of additional sanitary groups in the space identified by the school administration. Additionally, the design should include specification for improvement of the functional sanitary groups (Installation of soap dispensers, paper towel holders, hand dryers, replacement of broken faucets and water taps, and others as identified during the assessment).

- The design should also include accommodation of sanitary groups for persons with limited mobility.

- The design should address any structural and functional issues present in the existing sanitary facilities and handwash facilities including renewing flooring, walls, and ceilings, and ensuring that all elements meet current health, safety, and accessibility standards. Considerations should also include upgrading plumbing and sanitary facilities, water supply system, sewerage systems, renovating fixtures and fittings, improving heating and ventilation, electrical system, installation of water heaters, handwashing facilities, waste management, aesthetic, and functional improvements, ensuring accessibility for persons with disabilities, and adhering to relevant building codes and regulations.

- Additionally, prioritize the use of sustainable and durable materials to enhance the longevity and efficiency of the rehabilitated sanitary groups.

GTS at 1st floor (girls and staff)

GTS 2nd floor (boys and staff)

washbasins on the hallway

| Space for GTS near the sports hall Washbasins and GTS canteen area Proposed additional space for GTS at the 1st floor (archive) |  |
| --- | --- |

Photo 49                                                       Photo 50

Photo 51 Photo 52

R. Briceni, s. Larga ID 80

The school building was commissioned in 1968. The study block represents a building with three levels, the event and sports hall are separate from the study block. Due to the low number of children, the third level is preserved. The institution also manages a student dormitory with one level, accessible from the cafeteria area.

Rehabilitation works of the sanitary groups were carried out in 2007 for the primary school block at level 1, which has 10 cubicles (3 for girls, 3 for boys, all of which are defective, 3 urinals, one each for teachers, and 2 in the dormitory).

Hot water is only available from a boiler installation in the dormitory and in the sanitary groups for teachers. There are 18 handwashing facilities access points, (2 for teachers, 2 for girls, 2 for boys, 1 in the hallway, 8 near the cafeteria, and 3 in the dormitory). The dormitory has 2 showers, but they are defective.

Outside the sanitary groups, there are 8 washbasins near the cafeteria and one washbasin in the common area in the hallway.

Drinking water is supplied through a contract with the local public administration (APL), with costs covered by the municipality. The water is provided from a well on the school premises. Water testing was conducted in August 2023 and meets drinking water standards. The institution does not have water filters. The locality does not have a centralized sewage system or sewage treatment plant. Wastewater from the sanitary groups and cafeteria is discharged into a tank built in 1980, wastewater is not discharged.

Table 34 Demographics of school, r. Briceni, s. Larga

| Boys | 112 |
| --- | --- |
| Girls | 128 |
| Pupils with disabilities | CES – 4 |
| Total pupils | 240 |
| Teaching staff | 21 |
| Other staff | 10 |
| Total Staff | 31 |

Particular recommendations to take into consideration for selected location (but not limited to these):

- Develop the detailed design of the wastewater treatment plant (WWTP) and connection to building sewerage system to ensure efficient treatment of wastewater from the sanitary facilities. Including connection of wastewater and water pipes for constructed sanitary groups.

- Develop the detailed design for construction of sanitary groups from proposed existing spaces, located at 2nd floor for girls, boys and staff with all installation and pipe system connection. The design should also include rehabilitation of the sanitary groups and shower cabin in the existing spaces in locker room of sports hall for boys and girls, with all installations and pipe system connection.

- Develop the detailed design for renovation of sanitary groups for girls and boys at 1st, 2nd and 3rd floor, (toilet seats, door locks, water heaters, tiles, ventilation system, illumination system, mirrors, soap dispensers and paper holders, washbasins for smaller students), for staff at 1st floor (soap dispensers and paper holder, mirror, faucet, ventilation system, illumination system, trash bin for menstrual hygiene), for male staff at 1st floor (soap dispensers and paper holder, mirror and toilet seats installation)

- The design should also foresee installation of waters heaters for handwashing facilities near cafeteria, installation of 3 washbasins for smaller students, soap and paper holder, mirror, hand dryers. Washbasin installation in medical cabinet. Installation of 2 shower cabins for kitchen and dormitory staff sanitary groups.

- The design should address any structural and functional issues present in the existing sanitary facilities and handwash facilities including renewing flooring, walls, and ceilings, and ensuring that all elements meet current health, safety, and accessibility standards. Considerations should also include upgrading plumbing and sanitary facilities, water supply system, sewerage systems, renovating fixtures and fittings, improving heating and ventilation, electrical system, installation of water heaters, handwashing facilities, waste management, aesthetic, and functional improvements, ensuring accessibility for persons with disabilities, and adhering to relevant building codes and regulations.

- Additionally, prioritize the use of sustainable and durable materials to enhance the longevity and efficiency of the rehabilitated sanitary groups.

Canteen entrance – installation of 3 washbasins for small children, soap dispensers and paper holders, mirrors, water heaters, hand dryers

GTS boys classes 1-4 floor 1 – 3 toilet bowls, water heaters, installation of 3 urinals and separation wall, installation of 2 washbasins for small children, soap dispensers and paper holders, mirror installation

GTS boys classes 1-4 floor 1 – 3 toilet bowls, water heaters, installation of 3 urinals and separation walls, installation of 2 washbasins for small children, soap dispensers and paper holders, mirror installation

2nd Floor – rehabilitation/construction of sanitary groups for boys in the existing spaces including renewing flooring, walls, and ceilings, and ensuring that all elements meet current health, safety, and accessibility standards. Considerations should also include upgrading water supply system, sanitation system, plumbing and sewerage systems, renovating fixtures and fittings, improving ventilation, electrical system, installation of water heaters, handwashing facilities, waste management, aesthetic, and functional improvements, ensuring accessibility for persons with disabilities, and adhering to relevant building codes and regulations

GTS girls classes 1 - 4 floor 1 – 3 replace toilet bowls, door repairs - 3 pcs, water heaters installation, wall repairs, ventilation system installation, rehabilitation of lighting system, soap dispensers and paper holders, mirror installation hand dryers, 2 washbasins for small children

2nd floor – rehabilitation/construction of sanitary groups for boys in the existing spaces including renewing flooring, walls, and ceilings, and ensuring that all elements meet current health, safety, and accessibility standards. Considerations should also include upgrading water supply system, sanitation system, plumbing and sewerage systems, renovating fixtures and fittings, improving ventilation, electrical system, installation of water heaters, handwashing facilities, waste management, aesthetic, and functional improvements, ensuring accessibility for persons with disabilities, and adhering to relevant building codes and regulations

GTS school staff 1st floor – replacement of toilet bowl, installation of soap dispensers, paper holders, mirrors, hand dryer, ensuring accessibility for persons with disabilities.

2nd floor – rehabilitation/construction of sanitary groups for teachers in the existing spaces including renewing flooring, walls, and ceilings, and ensuring that all elements meet current health, safety, and accessibility standards. Considerations should also include upgrading water supply system, sanitation system, plumbing and sewerage systems, renovating fixtures and fittings, improving ventilation, electrical system, installation of water heaters, handwashing facilities, waste management, aesthetic, and functional improvements, ensuring accessibility for persons with disabilities, and adhering to relevant building codes and regulations

GTS school staff 1st – installation of soap dispensers, paper holders, mirrors, waters taps, hand dryers, ventilation system, lighting system, trash bin for menstrual hygiene, ensuring accessibility for persons with disabilities

2nd floor – rehabilitation/construction of sanitary groups for teachers in the existing spaces including renewing flooring, walls, and ceilings, and ensuring that all elements meet current health, safety, and accessibility standards. Considerations should also include upgrading water supply system, sanitation system, plumbing and sewerage systems, renovating fixtures and fittings, improving ventilation, electrical system, installation of water heaters, handwashing facilities, waste management, aesthetic, and functional improvements, ensuring accessibility for persons with disabilities, and adhering to relevant building codes and regulations

GTS kitchen staff - installation of soap dispensers, paper holders, mirrors, hand dryers, replacement of 2 shower cabins

Sports hall shower room girls

Sports hall GTS girls

Sports hall shower room boys

Sports hall GTS boys

Locker room boys Sports hall – common space and the locker room for girls and boys – change the destination and construction of GTS and shower cabins

R. Fălești, s. Glinjeni, ID 86

The school represents a 3-sorey block built in 1960. The school operates in a shift, with a total number of 226 students, of which girls 113, boys 113.

In 2012 sanitary groups were repaired inside the building. In total there are 9 toilet cubicles, of which only 7 are functional. The ventilation system in the sanitary groups is not functional.

The institution is connected to a centralized water supply system, but has no connection to the centralized sewerage system, wastewater and waste being discharged in the cesspit/tank and emptied with a special vehicle monthly. The canteen is not equipped with a grease separator.

Currently functional toilets are in satisfactory condition, but require some improvement, namely: Local repair of walls, installation of soap dispensers, paper holders, hand dryers, mirrors, installation of urinals, replacement of broken faucets, repair of door locking systems at toilet cabin, replacement of defective / non-standard sinks and other equipment as identified during the initial assessment.

Table 12 Demographics of school, r. Fălești, s. Glinjeni

| Boys | 113 |
| --- | --- |
| Girls | 113 |
| Pupils with disabilities | 0 |
| Total pupils | 226 |
| Teaching staff | 22 |
| Other staff | 18 |
| Total Staff | 40 |

Particular recommendations to take into consideration for selected location (but not limited to these):

- Develop the detailed design of the wastewater treatment plant (WWTP) and connection to building sewerage system to ensure efficient treatment of wastewater from the sanitary facilities. Including connection of wastewater and water pipes for constructed sanitary groups.

- Develop the detailed design for construction of sanitary groups near sports hall and in non-functional toilets spaces.

- The design should include also specification for renovation of functional sanitary groups with improvements, namely: installation of soap dispensers, paper holders, local repair of walls, installation of urinals, replacement of broken faucets, repair of door locking systems at toilet cabins, replacement of defective/ non-standard sinks, connection of hot water to sinks at all levels, installation of hand dryers and mirrors.

- The design should address any structural and functional issues present in the existing sanitary facilities and handwash facilities including renewing flooring, walls, and ceilings, and ensuring that all elements meet current health, safety, and accessibility standards. Considerations should also include upgrading plumbing and sanitary facilities, water supply system, sewerage systems, renovating fixtures and fittings, improving heating and ventilation, electrical system, installation of water heaters, handwashing facilities, waste management, aesthetic, and functional improvements, ensuring accessibility for persons with disabilities, and adhering to relevant building codes and regulations.

- Additionally, prioritize the use of sustainable and durable materials to enhance the longevity and efficiency of the rehabilitated sanitary groups.

| Photo 66 | Photo 67 |
| --- | --- |
| Photo 68 |  |

GTS 1st floor (boys)

GTS 1st floor (girls)

GTS School staff

| Washbasins hallway Space proposed for construction of new sanitary groups |  |
| --- | --- |

R. Căușeni, s. Coșcalia ID 112

The institution consists of 2 blocks, one with 1 level and 2 levels, built in 1967. The school operates in a shift, the total number of students being 176, of which girls 95, boys 81. The total number of employees is 26 people (20 women and 6 men). The institution has technical-sanitary blocks inside the building, their construction took place in 2022. The school is equipped with a centralized water system. The price for centralized water is 13 lei/m3. Wastewater is collected in a cesspool-type tank, and its cleaning is done once every 2 months. The price of a cleaning is 1000 lei. Toilet paper is present in all toilets, soap is also in washbasins. Near the cafeteria and in the corridor, there are 4 washbasins, equipped with soap.     The canteen is not equipped with a grease separator.

Table 46 Demographics of school,  r. Căușeni, s. Coșcalia

| Boys | 101 |
| --- | --- |
| Girls | 81 |
| Students with limited mobility | 95 |
| Total Students | 0 |
| Teaching staff | 176 |
| Technical staff | 16 |
| Total Staff | 10 |

Particular recommendations to take into consideration for selected location (but not limited to these):

- Develop the detailed design of the wastewater treatment plant (WWTP) and connection to building sewerage system to ensure efficient treatment of wastewater from the sanitary facilities. Including connection of wastewater and water pipes for constructed sanitary groups.

- The design should also foresee installation of hand dryers, mirrors for handwash basins, soar dispenser.

- The design should also include accommodation of sanitary groups for persons with limited mobility.

- Additionally, prioritize the use of sustainable and durable materials to enhance the longevity and efficiency of the rehabilitated sanitary groups.

R. Basarabeasca, or. Basarabeasca, ID 11

Public Institution Ivan Bondarev Gymnasium is divided into the primary school and the gymnasium, each located in separate buildings situated in different locations.

The primary school consists of a two-storey building. Within the institution, there are two sanitary groups: one located on the first floor for girls and the other on the second floor for boys. Both students and staff use these shared facilities. The sanitary groups require comprehensive repairs, including plumbing repairs to address any leaks or malfunctions, refurbishment of the interior walls, including tiling and painting, enhancements to ensure adequate privacy for users.

The water at the distribution points is potable. The interior sewerage system is connected to the locality's centralized sewerage system.

Gymnasium block is designed in two levels. In the institution is carried out capital repair of sanitary groups. Students and staff use the shared spaces and the outdoor sanitary groups at 150 m. Water at distribution points is drinking water. The sanitary groups in which capital repair is carried out cannot be used due to the missing connection with the locality centralized sewerage system. Wastewater is stored in the cesspit/tank. Emptying services have not been provided in recent years. Sanitary groups are not accessible for students with limited mobility.

Table 4 Demographics of school r. Basarabeasca, or. Basarabeasca

| Boys | 89 |
| --- | --- |
| Girls | 78 |
| Pupils with disabilities | 1 |
| Total pupils | 167 |
| Teaching staff | 12 |
| Other staff | 12 |
| Total Staff | 24 |

Particular recommendations to take into consideration for selected location (but not limited to these):

- Develop the detailed design for connection of school wash facilities to the local centralized sewerage system, which includes the construction of both interior and exterior sewage networks, the installation of a sewage pumping system to compensate elevation differences, and all necessary components.

- Develop the detailed design for construction of sanitary groups for persons with limited mobility in both primary school and gymnasium block.

- The design should also foresee:

- requirements for improvement of lighting, ventilation and heating systems in the existing sanitary groups.

- renovation of handwash facilities area that includes replacement of sinks, taps, soap dispensers, paper holders, mirrors, hand dryers and installation of water heaters.

- For primary school the design should include also the improvement of privacy situation in the existing sanitary groups that includes walls and doors with locks and increase the number of cabins at 1st and 2nd floors for girls and boys.

- The design should address any structural and functional issues present in the existing sanitary facilities and handwash facilities including renewing flooring, walls, and ceilings, and ensuring that all elements meet current health, safety, and accessibility standards. Considerations should also include upgrading plumbing and sanitary facilities, water supply system, sewerage systems, renovating fixtures and fittings, improving heating and ventilation, electrical system, installation of water heaters, handwashing facilities, waste management, aesthetic, and functional improvements, ensuring accessibility for persons with disabilities, and adhering to relevant building codes and regulations.

- Additionally, prioritize the use of sustainable and durable materials to enhance the longevity and efficiency of the rehabilitated sanitary groups.

Primary school

GTS level 2 boys GTS level 1 girls

Handwashing facilities, canteen access Handwashing facilities in cabinets

| GTS level 1 boys | GTS level 1 girls |
| --- | --- |
| Handwashing facilities GTS common access |  |
| Cafeteria access area, toilet washing facilities |  |
| Outdoor sanitary blocks |  |
| Outdoor sanitary blocks |  |

GTS level 1

mun. Chișinău, com. Bubuieci ID 34

The high school represents a construction composed from 3 blocks built in 1974. The school operates in 2 shifts, with the schedule: shift I) 08:00 - 12:45, shift II) 14:00 - 19:00. The total number of attending students is 1113, of which 521 are girls and 592 are boys. There are also 98 employees: 85 women and 13 men.

There are 20 toilets inside the buildings, all of which are functional, but not sufficient in number. The high school also accommodates students with reduced mobility, but there is no adapted sanitary group for them. The institution is connected to the centralized water and sewage system. Hot water supply is provided by electric heating boilers. The cafeteria is not equipped with a grease separator.

Table 44 Demographics of school, mun. Chișinău, com. Bubuieci

| Boys | 592 |
| --- | --- |
| Girls | 521 |
| Students with limited mobility | 1 |
| Total Students | 1113 |
| Teaching staff | 72 |
| Technical staff | 26 |
| Total Staff | 98 |

Particular recommendations to take into consideration for selected location (but not limited to these):

- Develop the detailed design for the construction of new sanitary groups in the existing spaces proposed by the school administration, with the aim of increasing the number of toilet cubicles.

- The design should also foresee specifications for renovation of the existing sanitary groups including reparation/replacement of the non-compliant washbasins, replacement of faucets, replacement of the doors, Installing soap dispensers, paper holders, mirrors and hand dryers in necessary locations. In addition, it is necessary to replace faucets and sinks in the corridors.

- The design should also include accommodation of sanitary groups for persons with limited mobility.

- The design should address any structural and functional issues present in the existing sanitary facilities and handwash facilities including renewing flooring, walls, and ceilings, and ensuring that all elements meet current health, safety, and accessibility standards. Considerations should also include upgrading plumbing and sanitary facilities, water supply system, sewerage systems, renovating fixtures and fittings, improving heating and ventilation, electrical system, installation of water heaters, handwashing facilities, waste management, aesthetic, and functional improvements, ensuring accessibility for persons with disabilities, and adhering to relevant building codes and regulations.

- Additionally, prioritize the use of sustainable and durable materials to enhance the longevity and efficiency of the rehabilitated sanitary groups.

GTS at the ground floor of the high school block (Staff and boys)

GTS At the ground floor of the high school block (Girls)

2nd floor WC accounting

3rd floor WC Staff

Handwash facilities near dining

WC Medical point

WC dining, same as in the workshop

Primary school classes WC 1st floor

| Primary school classes 1st floor Proposed space in the high school block on the 1st floor for execution GTS Proposed space in the workshop for new sanitary groups |  |
| --- | --- |

Sanitary group plans

UTA Găgăuzia, mun. Comrat ID 38

The Public Institution "Mihai Eminescu" Theoretical High School was commissioned in 1987 and represents a construction designed in 2 levels. Currently, a new block connected to the existing building has been build and is scheduled to be commissioned soon.

The institution is connected to the centralized water distribution system and centralized sewerage system, having a service contract for water and sewage with a single provider ("Apa Termo" from Ceadîr-Lunga). The water supplied at the distribution points does not meet potable water standards and is used only as technical water. The institution does not have water filters. Drinking water is provided in bottles in the hallway.

The indoor sanitary groups are accessible to younger children and for people with limited mobility at 1st floor. There are in total 12 toilet cubicles and 12 handwashing access points available. Ventilation and heating system in the sanitary groups is functional. Hot water is available for one single sanitary group (shared by teachers and administrative staff). Renovation works of the sanitary groups at 1st floor have been carried out recently and require only some small reparation works.

Table 28 Demographics of school, UTA Găgăuzia, mun. Comrat

| Boys | 246 |
| --- | --- |
| Girls | 341 |
| Pupils with disabilities | 3 |
| Total pupils | 587 |
| Teaching staff | 45 |
| Other staff | 17 |
| Total Staff | 62 |

Particular recommendations to take into consideration for selected location (but not limited to these):

- Develop the detailed design for reparation/construction of sanitary groups at 2nd floor (right wing) from the existing spaces, including all installations and pipe system connection.

- The design should also include specifications for renovation of the existing sanitary groups and handwash facilities that includes water heaters installation, soap dispensers and paper holders, mirrors, trash bins and menstrual hygiene bins.

- The design should address any structural and functional issues present in the existing sanitary facilities and handwash facilities including renewing flooring, walls, and ceilings, and ensuring that all elements meet current health, safety, and accessibility standards. Considerations should also include upgrading plumbing and sanitary facilities, water supply system, sewerage systems, renovating fixtures and fittings, improving heating and ventilation, electrical system, installation of water heaters, handwashing facilities, waste management, aesthetic, and functional improvements, ensuring accessibility for persons with disabilities, and adhering to relevant building codes and regulations.

- Additionally, prioritize the use of sustainable and durable materials to enhance the longevity and efficiency of the rehabilitated sanitary groups.

SG 1st floor girls (7-10)

SG 1st floor boys (7-10) SG 1st floor boys (7-10)

SG 1st floor for persons with reduces mobility (7-10)

SG 2nd floor girls (7-10)

SG 2nd floor boys (7-10)

SG 2nd floor for teachers SG 2nd floor for teachers

SG 1st floor girls (10-18) SG 1st floor girls (10-18)

SG 1st floor boys (10-18) SG 1st floor boys (10-18)

SG 1st floor for persons with reduced mobility (10-18)

Proposed space for SG 2nd floor girls / boys (10-18)

R. Căușeni, or. Căușeni, ID 47

The institution consists of a three blocks complex. In 2022, water network on the 1st and 2nd floors were partially renovated and connected to the local water distribution system.

The water source is the local centralized pipeline. Water is tested at the beginning of the school year in August. Based on results, water is used both as technical and drinking water. Water filters are installed at the counter, before the institution pipeline system in the school. The sewage system is connected to the locality centralized system. According to the initial assessment, also the sewage pipe system needs renovation.

The sanitary groups for primary classes for boys and girls on the 1st floor were partially renovated in 2017. However, they do not meet the minimum quality standards and require additional renovation. In 2022, one sanitary group for people with limited mobility was built on the 1st floor. On the 2nd floor, there are existing spaces intended for sanitary groups, according to the school's plans. Currently, only partially piping has been carried out for these sanitary groups. To cover all the needs, the construction of four sanitary groups is required in addition: one for boys, one for girls, and two for staff. Sanitary groups for kitchen staff need renovation as well.

The handwashing facilities near the dining room require renovation. Additional installation of sinks and hand dryers is needed. There is no hot water accessible at handwash facilities. Hot water is available in the kitchen and in an adjacent cabinet to the sanitary blocks on the 1st floor but is not connected to any washbasins. There is also an outdoor latrine toilet within the school premises.

Table 13 Demographics of school, r. Căușeni, or. Căușeni

| Boys | 237 |
| --- | --- |
| Girls | 228 |
| Pupils with disabilities | 1 |
| Total pupils | 465 |
| Teaching staff | 42 |
| Other staff | 14 |
| Total Staff | 56 |

Particular recommendations to take into consideration for selected location (but not limited to these):

- Develop the detailed design for construction of two sanitary groups in the existing spaces on the 2nd floor, for boys and staff, sanitary groups for kitchen staff in the existing spaces.

- Develop the detailed design for renovation of sanitary groups for girls and boys on the 1st floor, renovation of handwash facilities near cafeteria, including the entire spectrum of works (floor, cilling and walls repairs and finishing, new installation of sanitary equipment, also mirrors, soap dispensers and paper holders, hand dryers, water heaters).

- Investigate the need and possible solutions for water filters installation for drinking water.

- The design should address any structural and functional issues present in the existing sanitary facilities and handwash facilities including renewing flooring, walls, and ceilings, and ensuring that all elements meet current health, safety, and accessibility standards. Considerations should also include upgrading plumbing and sanitary facilities, water supply system, sewerage systems, renovating fixtures and fittings, improving heating and ventilation, electrical system, installation of water heaters, handwashing facilities, waste management, aesthetic, and functional improvements, ensuring accessibility for persons with disabilities, and adhering to relevant building codes and regulations.

- Additionally, prioritize the use of sustainable and durable materials to enhance the longevity and efficiency of the rehabilitated sanitary groups.

| 1st floor, SG for girls, primary school.. 1 st floor, SG for boys, primary school.. 1st floor, SG for persons with reduced mobility.. 1st floor, SG for staff.. 1st floor, boyler room. 2nd floor, existing space for SG for high school.. 2nd floor, existing space for SG for high school. 2nd floor, existing space for SG for high school.. Washbasins in the area for the cafeteria.. SG for kitchen staff. 1st floor, SG for boys. 1st floor, SG for girls.. 2nd floor, SG for boys and girls. 2nd floor, SG for boys, girls and staff... R. Ialoveni, s.Horești, ID 59 The school building was commissioned in 1974 and was originally designed to activate as kindergarten. The institution has two study blocks: one with two levels for middle school classes and the other with a single level for primary classes. The two-level study block has sanitary groups (constructed in 2013) located in the basement of the building that includes: toilet for girls with 3 cabins, 2 washbasins and hand dryer; toilets for boys with 3 cabins, 2 washbasins, 2 urinals and hand dryer; teachers have a separate cabin with a washbasin and toilet cabin. To note that the actual sanitary groups are not accommodated for persons with reduced mobility. The single-story block does not have sanitary groups for primary school children, (grade 1-4). Also, inside this block there is a training center for children with special needs, numbering 11 children. To accommodate the new sanitary groups within the building, a space currently used as a storage room has been identified. This will require changing the room's destination and constructing a new wastewater network. The locality has a centralized water supply system and centralized sewage system. Water testing took place in May 2023. Children are provided with drinking water from bottles placed in classrooms (18 in total) and common corridors (6 in total). There are 9 handwashing facilities, 5 in the larger block and 4 in the smaller one. Hot water is provided from boilers. Table 17 Demographics of school r.Ialoveni, s.Horești Boys; 151 (84, 1-4). Girls; 195 (66, 1-4). Pupils with disabilities; 11. Total pupils; 346. Teaching staff; 26. Other staff; 17. Total Staff; 43. Particular recommendations to take into consideration for selected location (but not limited to these): - Develop the detailed design for the rehabilitation/construction of the sanitary groups located within the primary school’s building, including modification and change the purpose of the existing storage spaces. - The design should also include specifications for small repairs of the existing WASH facilities, as appropriate, identified during the assessment. - The design should also include the adaptation of sanitary groups for persons with reduced mobility. - The design should address any structural and functional issues present in the existing sanitary facilities and handwash facilities including renewing flooring, walls, and ceilings, and ensuring that all elements meet current health, safety, and accessibility standards. Considerations should also include upgrading plumbing and sanitary facilities, water supply system, sewerage systems, renovating fixtures and fittings, improving heating and ventilation, electrical system, installation of water heaters, handwashing facilities, waste management, aesthetic, and functional improvements, ensuring accessibility for persons with disabilities, and adhering to relevant building codes and regulations. - Additionally, prioritize the use of sustainable and durable materials to enhance the longevity and efficiency of the rehabilitated sanitary groups. |  |
| --- | --- |

| GTS guys, necessary changing doors and rehabilitation of the ventilation system | GTS guys, necessary changing doors and rehabilitation of the ventilation system |
| --- | --- |
| GTS girls and staff, necessary to renovate ventilation and change doors for cabins | GTS girls and staff, necessary to renovate ventilation and change doors for cabins |
| GTS girls and staff, necessary to renovate ventilation and change doors for cabins | GTS girls and staff, necessary to renovate ventilation and change doors for cabins |
| Access washbasins canteen, it is necessary to repair and change washbasins |  |
| Change of storage room of products and dishes in GTS (girls, boys, staff and SEN) | Change of storage room of products and dishes in GTS (girls, boys, staff and SEN) |
| Change of storage room of products and dishes in GTS (girls, boys, staff and SEN) | Change of storage room of products and dishes in GTS (girls, boys, staff and SEN) |
| Rehabilitation of water points | Water points for pupils ages 7-10 |
| Kitchen room for washing dishes. | Sanitary group form female and male |

R.Călărași, s.Țibirica, ID 66

The Public Institution, Țibirica Middle School, represents a building designed in 4 blocks (Block A having 2 levels, Block B with 1 level, Block C with 3 levels, and Block D with 3 levels). The institution was commissioned in 1989. And was designed to serve as a school. The institution operates on a single-shift schedule.

The school is connected to the locality’s centralized sewerage system and water distribution system. Water at distribution points is drinking water, with a price for water services estimated at 12 lei/ m3. The canteen has filtration facilities.

The school has indoor sanitary groups. In 2017, the institution has developed a design project for renovation of the entire school. But due to insufficient funds, just some internal sanitary groups were renovated in 2019-2020, mainly: the sanitary groups in Block D – levels 1 and 3; and Block C – levels 1 and 3.  There are 20 functional hand washing facilities. Total number of cabins 18 pcs, functional 17pcs. Cabins for girls 8 pcs, boys 8 pcs and staff 2 pcs. Access for students with limited mobility is difficult. The sanitary groups for teachers in block C have incorrect sewage connections, leading to leaks, washbasin are not connected to hot water. In the sanitary groups for boys in block D level 3, are functional 2 cabins out of 3. In addition, sanitary groups for boys (primary school) does not provide enough privacy to students. In the sanitary groups for girls (primary school), hot water is not connected to the washbasins. In addition, sanitary bins for the disposal of menstrual hygiene products are missing, toilet paper holder in each cabin is missing.

Table 18 Demographics of school r.Călărași, s.Țibirica

| Boys | 162 |
| --- | --- |
| Girls | 132 |
| Pupils with disabilities | 3 |
| Total pupils | 294 |
| Teaching staff | 23 |
| Other staff | 20 |
| Total Staff | 43 |

Particular recommendations to take into consideration for selected location (but not limited to these):

- Develop the detailed design for rehabilitation/construction of the sanitary group for the students located within the building, alongside with the reparation of non-functional showers in the sports hall.  Ensure seamless connectivity with the locality’s sewerage system to facilitate efficient management of wastewater from the sanitary facilities.

- The design should address any structural and functional issues present in the existing sanitary facilities and handwash facilities including renewing flooring, walls, and ceilings, and ensuring that all elements meet current health, safety, and accessibility standards. Considerations should also include upgrading plumbing and sanitary facilities, water supply system, sewerage systems, renovating fixtures and fittings, improving heating and ventilation, electrical system, installation of water heaters, handwashing facilities, waste management, aesthetic, and functional improvements, ensuring accessibility for persons with disabilities, and adhering to relevant building codes and regulations.

- Additionally, prioritize the use of sustainable and durable materials to enhance the longevity and efficiency of the rehabilitated sanitary groups.

| GTS Level 1 Block D | GTS Level 1 Block D |
| --- | --- |
| GTS Level 1 Block D, girls | GTS Level 1 Block D, girls |
| GTS Level 2 Block D | GTS Level 2 Block D |
| GTS Level 2 Block D | GTS Level 2 Block D |
| GTS level 2 Block D, shower/toilet | GTS level 2 Block D, shower/toilet |
| GTS level 2 Block D, shower/toilet | GTS level 2 Block D, shower/toilet |
| GTS Level 3 Block D | GTS Level 3 Block D |
| GTS Level 3 Block D | GTS Level 3 Block D |
| GTS level 1 Block C, teachers | GTS level 1 Block C, teachers |
| GTS level 1 Block C, teachers | GTS Level 1 Block C |
| GTS Level 1 Block C | GTS Level 1 Block C |
| GTS Level 2 Block C, boys | GTS Level 2 Block C, boys |
| GTS Level 2 Block C, boys | GTS Level 3 Block C, girls |
| GTS Level 3 Block C, girls | GTS Level 1 Block B |
| GTS Level 1 Block B | GTS Level 1 Block B |
| Handwashing facilities - canteen access | GTS kitchen staff |
| GTS Level 1 Block A | GTS Level 1 Block A |
| Boys locker room, level 1 | Boys locker room, level 1 |
| Girls locker room, level 1 | Girls locker room, level 1 |
| Boys locker room, level 2 | Boys locker room, level 2 |
| Girls locker room, level 1 | Girls locker room, level 1 |
| Block A shower area |  |

| Sanitary group, block D, floor 1 | Sanitary group, block D, floor 2 |
| --- | --- |

| Sanitary group, block D, floor 2 | Sanitary group, block D, floor 2 |
| --- | --- |
| Sanitary group, block D, floor 2 | Sanitary group, block D, floor 3 |
| Sanitary group, block C, floor 1 | Sanitary group, block B, floor 1 |
| WC for kitchen staff | Sanitary group, block A, floor 1 |
| Locker room with showers for male, floor 1 | Locker room with showers for female, floor 1 |
| Locker room with showers for male, floor 2 | Locker room with showers for female, floor 2 |
| Showers, block A, floor 2 |  |

R. Rezina, s. Ignăței, ID 73

The Ioan Sarbu Theoretical High School Public Institution is designed in 3 floors and was put into operation in 1986. . The Public Institution is divided into three stages: primary grade, gymnasium grade and high school grade.  Staff and students at primary, secondary and high school level use the shared sanitary groups.

The institution has 8 indoor sanitary groups. Functional: level 1 – sanitary groups arranged for girls, level 2 – sanitary groups for teachers, level 3 – sanitary groups for boys and sanitary groups in the kitchen for kitchen staff. Sanitary groups for girls level 1, boys level 3 and teachers level 2 have been renovated in 2017. However, sanitary facilities for persons with reduced mobility are missing. Additionally, the designated area for menstrual hygiene, bins for menstrual hygiene products, and paper holders are also absent. Primary, middle, and high school students use the same sanitary groups. Two sanitary groups are used as a warehouse, archive. Sanitary groups in the locker rooms need general renovation.

The institution is connected to the centralized water supply system and water is delivered to the building. The drinking water distribution points are 13 total/functional Water at distribution points is potable.

In 2023 the internal sewerage network has been partially renovated. Wastewater is discharged into the cesspit/tank located on the premises of the institution. It is important to note that, as of the assessment date, the construction of the sewerage network is in progress in the locality, and the connection of the school infrastructure to this network should be considered.

Table 7 Demographics of school, r. Rezina, s. Ignăței

| Boys | 137 |
| --- | --- |
| Girls | 132 |
| Pupils with disabilities | 0 |
| Total pupils | 269 |
| Teaching staff | 33 |
| Other staff | 22 |
| Total Staff | 55 |

Particular recommendations to take into consideration for selected location (but not limited to these):

- Develop the detailed design for connecting the school's wastewater system to the new sewerage network currently under construction in the locality. Alternative, design of the wastewater treatment plant (WWTP) and connection to building sewerage system to ensure efficient treatment of wastewater from the sanitary facilities. Including connection of wastewater and water pipes for constructed sanitary groups.

- Develop the detailed design for construction of sanitary groups at 1st, 2nd, and 3rd floors, in locker room and in kitchen, for kitchen staff in the existing spaces. In addition to include construction of one sanitary group for people with limited mobility and one menstrual hygiene cabin for girls.

- Develop the detailed design for renovation of sanitary groups, including installation of hot water source (boiler), toilet paper holders, soap dispensers and hand dryers. Design and construction of a ventilation system for WASH facilities.

- The design should address any structural and functional issues present in the existing sanitary facilities and handwash facilities including renewing flooring, walls, and ceilings, and ensuring that all elements meet current health, safety, and accessibility standards. Considerations should also include upgrading plumbing and sanitary facilities, water supply system, sewerage systems, renovating fixtures and fittings, improving heating and ventilation, electrical system, installation of water heaters, handwashing facilities, waste management, aesthetic, and functional improvements, ensuring accessibility for persons with disabilities, and adhering to relevant building codes and regulations.

- Additionally, prioritize the use of sustainable and durable materials to enhance the longevity and efficiency of the rehabilitated sanitary groups.

| 1st floor WASH facilities | 2nd floor WASH facilities |
| --- | --- |
| 3rd floor WASH facilities | Existing situation locker rooms |
| Proposed locker rooms | 28 Kitchen area |

Level 1 GTS girls Level 1 GTS girls

Level 2 GTS teachers Level 2 GTS teachers

Level 3 GTS boys

Level 3 GTS

Level 2 GTS

Girls locker room

Boys locker room

Install hand washing – canteen access

Personal toilet, kitchen

Personal shower, kitchen

R. Anenii Noi, s.Mereni, ID 74

The primary school in Mereni host students aged 6 to 11. Built between 1965 and 1970, the institution accommodates both kindergarten children and elementary school students. Currently, sanitary groups are only available on the ground floor of the building, serving both students and kindergarten children. However, these facilities are not adapted for people with limited mobility. The second floor of the building is non-functional due to major structural issues, such as the deterioration of the floor in one of the classrooms, leading to the closure of the entire floor. The school has space that could be converted into sanitary groups for students. In terms of infrastructure, the institution is connected to the local centralized water supply system and the centralized sewage network.

Table 31 Demographics of school

| Boys | 246 |
| --- | --- |
| Girls | 120 |
| Pupils with disabilities | 0 |
| Total pupils | 366 |
| Teaching staff | 37 |
| Other staff | 2 |
| Total Staff | 39 |

Particular recommendations to take into consideration for selected location (but not limited to these):

- Develop the detailed design for rehabilitation of sanitary blocks on 2nd floor.

- Develop the detailed design for construction of the sanitary groups in the space identified by the school administration. Ensure seamless connectivity with the sewage system to facilitate efficient management of wastewater from the sanitary facilities.

- In addition, the design should foresee the construction of one sanitary group for people with limited mobility and one menstrual hygiene cabin for girls.

- The design should address any structural and functional issues present in the existing sanitary facilities and handwash facilities including renewing flooring, walls, and ceilings, and ensuring that all elements meet current health, safety, and accessibility standards. Considerations should also include upgrading plumbing and sanitary facilities, water supply system, sewerage systems, renovating fixtures and fittings, improving heating and ventilation, electrical system, installation of water heaters, handwashing facilities, waste management, aesthetic, and functional improvements, ensuring accessibility for persons with disabilities, and adhering to relevant building codes and regulations.

- Additionally, prioritize the use of sustainable and durable materials to enhance the longevity and efficiency of the rehabilitated sanitary groups.

| WC floor 1 | WC floor 1 |
| --- | --- |

| GTS level 1 | GTS level 1 |
| --- | --- |
| Proposed space for change of destination |  |
| School plan |  |

R.Orhei, s.Ghetlova, ID 103

The school is equipped with indoor sanitary facilities spread across two levels. However, these facilities are in varied states of condition and compliance with necessary standards. The following details highlight the current status and needs of the sanitary groups in the school:

Current Condition of Sanitary Facilities

Level 1 Sanitary Groups:

Renovated but lacking a ventilation system.

Do not comply with standards for accessibility for persons with reduced mobility.

Insufficient number of washbasins in the boys' sanitary block.

Level 2 Sanitary Groups:

Require complete renovation.

Currently lack a ventilation system.

Specifically, the sanitary groups on the 2nd floor require rehabilitation of the water supply and sewerage networks, which are old and have not been used since the school's construction.

Water and Sewage Systems

The school is connected to a centralized water supply and sewage system.

Water is tested at the beginning of the academic year and deemed suitable for technical use, but not for drinking. Drinking water is therefore supplied in bottles.

The sewerage system is centralized.

Additional Facilities

There is an external toilet facility on the school premises.

Budget and Planning

The school administration has prepared a budget for renovating the sanitary groups on Level 2.

Conclusion and Recommendations

To ensure all sanitary facilities within the school meet the required standards and provide a safe and functional environment for students and staff, the following actions are recommended:

Ventilation Systems: Install appropriate ventilation systems in both the renovated sanitary groups on Level 1 and the sanitary groups to be renovated on Level 2.

Accessibility Compliance: Upgrade the renovated sanitary groups on Level 1 to comply with accessibility standards for persons with reduced mobility.

Increase Washbasins: Add additional washbasins to the boys' sanitary block on Level 1 to meet the required number.

Renovate Level 2 Sanitary Groups: Proceed with the planned renovation of the sanitary groups on Level 2, ensuring the rehabilitation of the water supply and sewerage network.

Table 45 Demographics of school, r.Orhei, s.Ghetlova

| Boys | 101 |
| --- | --- |
| Girls | 81 |
| Students with limited mobility | 0 |
| Total Students | 182 |
| Teaching staff | 21 |
| Technical staff | 7 |
| Total Staff | 28 |

Particular recommendations to take into consideration for selected location (but not limited to these):

- Develop the detailed design for renovation of sanitary groups within the school and increase the number of toilets used by students. In addition, the design should include the installation of the ventilation system in the sanitary groups. Also, for sanitary groups from 2nd floor, rehabilitation of water supply and sewerage network is required.

- Develop the detailed design for construction of new sanitary groups in existing spaces proposed by school administration on 2nd floor for boys and for girls.

- Investigate the need and possible solutions for water filters installation for drinking water.

- The design should address any structural and functional issues present in the existing sanitary facilities and handwash facilities including renewing flooring, walls, and ceilings, and ensuring that all elements meet current health, safety, and accessibility standards. Considerations should also include upgrading plumbing and sanitary facilities, water supply system, sewerage systems, renovating fixtures and fittings, improving heating and ventilation, electrical system, installation of water heaters, handwashing facilities, waste management, aesthetic, and functional improvements, ensuring accessibility for persons with disabilities, and adhering to relevant building codes and regulations.

- Additionally, prioritize the use of sustainable and durable materials to enhance the longevity and efficiency of the rehabilitated sanitary groups.

| Toilet for girls, level 1.; Boys bathroom, level 1. Handwashing installations inside the dining room. Toilet for boys, level 2.. Current situation toilet for boys, level 2.; Current situation toilet for boys, level 2.. Sanitary block for girls, level 2.. Current situation toilet for girls, level 2.; Current situation toilet for girls, level 2.. |  |
| --- | --- |
| R. Cantemir, s. Țiganca, ID 107 The school, located in Tiganca village in the southern region of the Republic of Moldova, comprises a building with three blocks (wings) that was commissioned in 1965. Over the years, the school has undergone several rehabilitation projects to improve its facilities. Despite these efforts, there remain significant issues that need addressing to ensure the functionality and accessibility of the school's Water, Sanitation, and Hygiene (WASH) facilities. Rehabilitation works of the sanitary groups for girls and boys were carried out in 2010. Additionally, an annex (Block B-A) was constructed in 2006; however, this annex lacks both hot water and ventilation systems. There is also a critical need to construct sanitary groups for people with limited mobility to ensure inclusivity. Hot water is available through a boiler system at the sinks near the cafeteria, which includes a total of seven sinks. Drinking water is supplied from filtration facilities located in the canteen, though the faucets need replacement. The water from the central water supply system was tested in August 2023 and meets the minimum sanitation requirements for both drinking and technical purposes. The local public authorities oversee the distribution of drinking water. The locality has a centralized sewage system, to which only the school handwashing facilities from the kitchen are currently connected. Wastewater from the cesspool is pumped directly to the local sewage treatment plant using a pump, which incurs only electricity costs due to the proximity of the gymnasium. Current Facilities Handwashing Facilities: There are ten handwashing facilities in total: 1 sink in the boys' sanitary groups 1 sink in the girls' sanitary groups 1 sink in the teachers' sanitary groups 7 sinks near the cafeteria Toilet Cubicles: There are ten toilet cubicles: 4 for girls 3 for boys (plus 4 urinals) 3 for auxiliary staff and teachers However, these cubicles are not usable due to the lack of connection to the centralized sewage system. Handwashing facilities are not accessible to children with reduced mobility due to the absence of access ramps and guiding bars. They are also not suitable for younger children. Additionally, there are no sanitary groups available for people with disabilities. Table 24 Demographics of school, r. Cantemir, s. Țiganca Boys; 82. Girls; 96. Pupils with disabilities; 1. Total pupils; 178. Teaching staff; 16. Other staff; 16. Total Staff; 32. Particular recommendations to take into consideration for selected location (but not limited to these): - Develop the detailed design for construction of a pipeline system to connect existing sanitary groups constructed in 2010 and 2013 to the centralized sewerage system with treatment plant in the vicinity of the school. - Develop the detailed design for the renovation of the WASH facilities that includes: - Sanitary groups teachers and girls (block B-A) – it is necessary to install two more washbasins, ventilation system, a cabin for hygiene and menstruation of the woman, installation of water heaters. - Canteen access – adjust the height of three washbasins to facilitate access for younger students and install soap dispensers and hand dryers. Additionally, install two more washbasins and water heater. - Sanitary groups for girls – installation of ventilation system, heating, toilet paper holders and soap dispensers, additional installation of two more washbasins and water heaters. - GTS boys – installation of ventilation system, heating, toilet paper holders and soap dispensers, additional installation of two more washbasins, provide PVC walls for urinals to ensure privacy. - Accommodate shower cabins for girls and boys, taking space from the deposit room, and include all necessary installations and pipe system connections. - Construction of one sanitary group for people with limited mobility. - The design should address any structural and functional issues present in the existing sanitary facilities and handwash facilities including renewing flooring, walls, and ceilings, and ensuring that all elements meet current health, safety, and accessibility standards. Considerations should also include upgrading plumbing and sanitary facilities, water supply system, sewerage systems, renovating fixtures and fittings, improving heating and ventilation, electrical system, installation of water heaters, handwashing facilities, waste management, aesthetic, and functional improvements, ensuring accessibility for persons with disabilities, and adhering to relevant building codes and regulations. - Additionally, prioritize the use of sustainable and durable materials to enhance the longevity and efficiency of the rehabilitated sanitary groups. 1st floor; 2nd floor. |  |
| Canteen access | The institution water filtration system |
| SG boys |  |
| SG teachers and girls (block B-A) |  |
| SG girls |  |

R. Anenii Noi, s.Speia, ID 106

The Public Institution Speia Gymnasium, commissioned in 1984 as a two-level building initially designed for educational purposes, caters to students aged 7 to 16 years old and operates on a single shift. The institution comprises both primary and gymnasium levels.

Currently, the institution faces several challenges regarding its indoor Water, Sanitation, and Hygiene (WASH) facilities. There are a total of 8 interior sanitary groups, with only 3 of them renovated in 2019. The remaining 5 sanitary groups are repurposed for storage and archives, lacking essential upgrades. Notably, none of the sanitary groups are equipped with a ventilation system, and privacy within the toilet cubicles is insufficient for students. Moreover, facilities for menstrual hygiene are absent, and none of the existing sanitary groups are accessible for persons with reduced mobility.

The institution is connected to an old, centralized water supply and sewerage system, despite the recent installation of a new sewerage and water supply system nearby. Potable water is distributed through 9 points, with 7 currently functional. The boiler room underwent rehabilitation in 2023, enhancing heating capabilities.

In conclusion, significant improvements are necessary to ensure hygiene, accessibility, and comfort for students and staff. Addressing these deficiencies, including the installation of ventilation systems, privacy enhancements, provisions for menstrual hygiene, and accessibility upgrades, alongside leveraging the new water and sewerage systems, will enhance the overall functionality and safety of the institution.

.

Table 21 Demographics of school r.Anenii Noi, s.Speia

| Boys | 97 |
| --- | --- |
| Girls | 86 |
| Pupils with disabilities | 0 |
| Total pupils | 183 |
| Teaching staff | 15 |
| Other staff | 10 |
| Total Staff | 25 |

Particular recommendations to take into consideration for selected location (but not limited to these):

- Develop the detailed design for connection to the locality newly built water supply and sewage pipeline.

- Develop the detailed design for rehabilitation of all existing sanitary groups addressing the existing deficiencies, including the installation of ventilation systems, privacy enhancements, provisions for menstrual hygiene, and accessibility upgrades.

- The design should also include the adaptation of sanitary groups for persons with reduced mobility.

- The design should address any structural and functional issues present in the existing sanitary facilities and handwash facilities including renewing flooring, walls, and ceilings, and ensuring that all elements meet current health, safety, and accessibility standards. Considerations should also include upgrading plumbing and sanitary facilities, water supply system, sewerage systems, renovating fixtures and fittings, improving heating and ventilation, electrical system, installation of water heaters, handwashing facilities, waste management, aesthetic, and functional improvements, ensuring accessibility for persons with disabilities, and adhering to relevant building codes and regulations.

- Additionally, prioritize the use of sustainable and durable materials to enhance the longevity and efficiency of the rehabilitated sanitary groups.

| Sanitation block for male, 1st floor | Proposed Sanitation block for female, 2nd floor. |
| --- | --- |

| Sanitation block for kitchen staff. | Sanitation block, 1st floor. |
| --- | --- |

| GTS Level 1 girls students. |  | GTS Level 1 girls students. |
| --- | --- | --- |
| GTS Level 1 teachers. |  | GTS Level 1 teachers. |
| GTS Level 1 beaten students. |  | GTS Level 1 beaten students. |
| GTS Level 2 |  | GTS Level 2 |
| GTS Level 2 |  | Level 1, For GTS proposal for ESC people |
| Handwashing facilities - canteen access |  | Toilet for technical staff in the canteen |
| Shower for technical staff in the canteen |  | GTS girls locker room |
| GTS girls locker room |  | GTS girls locker room |
| GTS boys locker room | GTS boys locker room | GTS Level 3 right |

R. Hîncești, s.Bozieni, ID 120

Public Institution Bozieni Gymnasium, commissioned in 1965, serves both primary and gymnasium levels within a two-store building designed originally as a school. The institution operates on a single shift. Over time, the institution has faced challenges related to the functionality and accessibility of its indoor WASH (Water, Sanitation, and Hygiene) facilities.

The institution houses 8 indoor sanitary groups. Sanitary groups on level 1 are arranged for girls, boys and teachers. These sanitary groups were renovated in 2017 and comprise: four cabins for girls, two cabins for boys, three urinals and two cabins for teachers. On 2nd floor, sanitary groups are used as storage and archive. The sanitary groups in the locker rooms and canteen area for staff are not functional. The staff and students of the primary level use the sanitary groups located on level 1. Moreover, facilities for menstrual hygiene are absent, and none of the existing sanitary groups are accessible for persons with reduced mobility.

The institution is connected to the centralized water supply system, and water is delivered to the building. The water from the distribution points is technical water. There are a total of 8 functional drinking water distribution points.

A sewerage network is present in the locality, but wastewater is discharged into the cesspit/tank located on the premises of the school.

Table 23 Demographics of school r.Hîncești, s.Bozieni

| Boys | 89 |
| --- | --- |
| Girls | 79 |
| Pupils with disabilities | 1 |
| Total pupils | 168 |
| Teaching staff | 18 |
| Other staff | 12 |
| Total Staff | 30 |

Particular recommendations to take into consideration for selected location (but not limited to these):

- Develop the detailed design for connection of the school facilities to local sewerage system.

- Develop the detailed design for rehabilitation/improvement of sanitary groups inside the building on levels 1 and 2, and the locker rooms for staff in canteen.

- In addition, the design should foresee the construction of sanitary groups for persons with reduced mobility and also menstrual hygiene cabins for girls.

- The design should address any structural and functional issues present in the existing sanitary facilities and handwash facilities including renewing flooring, walls, and ceilings, and ensuring that all elements meet current health, safety, and accessibility standards. Considerations should also include upgrading plumbing and sanitary facilities, water supply system, sewerage systems, renovating fixtures and fittings, improving heating and ventilation, electrical system, installation of water heaters, handwashing facilities, waste management, aesthetic, and functional improvements, ensuring accessibility for persons with disabilities, and adhering to relevant building codes and regulations.

- Additionally, prioritize the use of sustainable and durable materials to enhance the longevity and efficiency of the rehabilitated sanitary groups.

| Level 1 GTS Girls/Boys - Common area at hand washing facilities |  |
| --- | --- |
| Level 1 GTS boys | Level 1 GTS boys |
| Level 1 GTS girls |  |
| Handwashing facilities - canteen access |  |
| GTS level 2 right GTS level 2 right |  |
| GTS small level 2 right | GTS small level 2 left |
| GTS level 2 left |  |
| Personal shower in the cafeteria | Personal toilet in the cafeteria |
| GTS boys locker room |  |
| GTS girls locker room |  |
| GTS level 1 left GTS level 1 left |  |
| GTS small level 1 left |  |

| Sanitary block proposed to enhance | Locker room |
| --- | --- |
| Toilets for female and stuff, floor 1,2 | Toilets for male and stuff, floor 1,2 |
| Shower area for kitchen staff |  |

- Taraclia, or. Taraclia, ID 76

The Public Institution "Taraclia" Gymnasium represents a one-store building. The age of the students ranges from 7 to 16 years old. The school program is operated in a single shift. General renovation works were carried out in 2016. The sanitary groups on the left wing are used only by girls and teachers. The sanitary groups on the right wing are used only by boys and teachers. Currently, the water source for the gymnasium is the centralized water system. Drinking water is accessible at the water distribution points. Wastewater is evacuated into the centralized sewage system. There are a total of 8 functional drinking water distribution points and 8 functional handwashing points. The institution has a water filtration system.

Table 16 Demographics of school, r. Taraclia, or. Taraclia

| Boys | 152 |
| --- | --- |
| Girls | 112 |
| Pupils with disabilities | 0 |
| Total pupils | 264 |
| Teaching staff | 31 |
| Other staff | 17 |
| Total Staff | 48 |

Particular recommendations to take into consideration for selected location (but not limited to these):

- Develop the detailed design for construction of sanitary groups for kitchen staff.

- The design should also include the renovation of existing sanitary groups for boys and girls.

- The design should address any structural and functional issues present in the existing sanitary facilities and handwash facilities including renewing flooring, walls, and ceilings, and ensuring that all elements meet current health, safety, and accessibility standards. Considerations should also include upgrading plumbing and sanitary facilities, water supply system, sewerage systems, renovating fixtures and fittings, improving heating and ventilation, electrical system, installation of water heaters, handwashing facilities, waste management, aesthetic, and functional improvements, ensuring accessibility for persons with disabilities, and adhering to relevant building codes and regulations.

- Additionally, prioritize the use of sustainable and durable materials to enhance the longevity and efficiency of the rehabilitated sanitary groups.

Access to the cafeteria for hand washing facilities

GTS level 1 left GTS level 1 left

GTS level 1 on the right GTS level 1 on the right

To propose toilet / shower for kitchen staff

Photo 16.1 Proposed sanitary block kitchen staff

The purpose of assessing existing buildings is either to maintain their original use, or to change their use.

In line with UNICEF’s Accessibility Technical Cards and Procedure on Eco-efficiency and Inclusive Access

In the case of UNICEF office construction/renovation/rehabilitation, engage with the Inclusive & Sustainable operations team to ensure compliance with the Procedure on Eco-Efficiency and Inclusive Access in UNICEF Facilities and Operations, including the cases where a green building certification is pursued.

Full architectural set includes master plan, layout, plans, sections, elevations, 3D images, details and finishes.

Full structural set includes foundation details, structural design and details of columns, beams, slabs, stairs, etc.

Such as owner’s permit, construction permit, environmental permit, permits from utility companies, including necessary design/drawings and documentation for service declaration to the government.

Duration depends on the tendering process.

After issuance of the Certificate of Substantial Completion.

Will be linked to the timeframe agreed in the construction contract.