## Technical Specifications
Annex 4: Technical specifications for equipment and goods
ITB26/03173: Reconstruction of the Indoor Shooting Range Facility of the 'Stefan cel Mare' Academy of the Ministry of Internal Affairs
No. | BOQ Ref. | Line No. | Type of equipment requested by BoQ and its data |  | Bidder’s response
[5 empty] | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
[5 empty] | Yes, we comply | No, we do not comply (indicate discrepancies)
|  |  | Incalzire, ventilare, conditionare (12/25-J-IVC) | Heating, Ventilation, Air Conditioning (12/25-J-IVC)
1 | 2-1-4 | 125 | Unitate de admisie si evacuare A+ cu mecanism rotativ recuperator, eficienta termica 76%, dimensiuni totale 1150x1150x2100, cu sistem de control automat C5 inclus: L=3240 m3/ora, P=661Pa, set complet: 1. Ventilator de admisie L=3240 m3/ora, P=661 Pa; 2. Ventilator de evacuare L=3240 m3/ora, P=653 Pa; 3. Filtru de admisie F7 dimensiune 525x510x92mm; 4. Filtru de pe hota M5 masoara 800x400x46 mm; 5. Schimbator de caldura cu doua fete DX-G10-03R-0895-0420-270/-10-1x03C 1x04C-26F-M1-CDE-IS1-RC-2x5/8/2x22-150 Qt=10.5 kW, Qx=7.1 kW; 6. Schimbator de caldura rotativ RR-AL-930-L-O-SN (1056x1058x290)-PN-A1, energie eficienta 76% N=0.096 kW; 7. Unitatea de control automata C5; 8. Telecomanda C5.1; 9. Senzor de calitate a aerului; 10. Senzor de temperatura exterioara; 11. Senzor de temperatura interna de tip VERSO-R-4000-UV-HCDX-R1-F7/M5-C5-L/A sau analog | Supply and exhaust unit A+ with rotary heat recovery wheel, thermal efficiency 76%, overall dimensions 1150x1150x2100, with automatic control system C5 included: L=3240 m3/h, P=661Pa, complete set: 1. Supply fan L=3240 m3/h, P=661 Pa; 2. Exhaust fan L=3240 m3/h, P=653 Pa; 3. Supply air filter F7 size 525x510x92 mm; 4. Hood filter M5 size 800x400x46 mm; 5. Double-sided heat exchanger DX-G10-03R-0895-0420-270/-10-1x03C 1x04C-26F-M1-CDE-IS1-RC-2x5/8/2x22-150 Qt=10.5 kW, Qx=7.1 kW; 6. Rotary heat exchanger RR-AL-930-L-O-SN (1056x1058x290)-PN-A1, energy efficiency 76%, N=0.096 kW; 7. Automatic control unit C5; 8. Remote controller C5.1; 9. Air quality sensor; 10. Outdoor temperature sensor; 11. Indoor temperature sensor type VERSO-R-4000-UV-HCDX-R1-F7/M5-C5-L/A or equivalent.
2 | 2-1-4 | 126 | Unitate exterioara pentru schimbator de caldura cu doua fete Qx=15.24 kW, Qt=18.17 kW. Temperatura aerului exterior la racire -15*C, incalzire la -20*C, Freon R32, N=7.5 kW, A++. Dimensiuni totale 952x415x1333h. Kit de ham KA8142, cu suporturi antivibratii pentru unitate exterioare MOU-55HFN8a-KA8142 sau analog | Outdoor unit for double-sided heat exchanger Qx=15.24 kW, Qt=18.17 kW. Outdoor air temperature: cooling -15C, heating -20C. Refrigerant R32, N=7.5 kW, A++. Overall dimensions 952x415x1333h. Wiring kit KA8142, with anti-vibration supports for outdoor unit MOU-55HFN8a-KA8142 or equivalent.
3 | 2-1-4 | 127 | Pompa de evacuare a condensului pentru aparate de aer conditionat cu o capacitate pina la 20 kW, consum de energie 19W, nivel de zgomot 26 dB, debit vertical max 12m de la pompa la iesire apa, dimensiuni pompa 62x30x55 mm, dimensiuni plutitor 67x32x38 mm tip EASY FLOW 20 l sau analog | Condensate drain pump for air conditioners with capacity up to 20 kW, power consumption 19W, noise level 26 dB, maximum vertical lift 12 m from pump to water discharge, pump dimensions 62x30x55 mm, float dimensions 67x32x38 mm, type EASY FLOW 20 l or equivalent.
4 | 2-1-4 | 128 | Clapeta cu actionare electromagnetica tip SRU-M-500x400+LF24 sau analog | Electromagnetic damper type SRU-M-500x400+LF24 or equivalent.
5 | 2-1-4 | 129 | Atenuator de zgomot STS-IVR3BA-800-500-700-S sau analog | Noise attenuator STS-IVR3BA-800-500-700-S or equivalent.
6 | 2-1-4 | 130 | Atenuator de zgomot STS-IVR3BA-800-500-1250-S sau analog | Noise attenuator STS-IVR3BA-800-500-1250-S or equivalent.
7 | 2-1-4 | 131 | Supapa ignifuga normal deschisa 200x150 | Normally open fire damper 200x150.
8 | 2-1-4 | 132 | Supapa ignifuga normal deschisa 150x150 | Normally open fire damper 150x150.
9 | 2-1-4 | 133 | Unitate de admisie si evacuare 15/09 pe admisie si 15/12 pe capota A+ stanga cu actionare rotativa recuperator si schimbator de caldura cu freon, eficienta termica 82% cu sectiuni de filtrare pentru un poligon de tragere. Dimensiuni totale 8443x1560x2655 sistemul de control automat C5 in set complet: L=14600 m3/ora, P=1208/1517 Pa, set complet. 1) Sectiune multifunctionala cu amortizor actionare electrica LM230A Belimo cu flexibilitate. 2) Sectiune de filtrare cu filtru de buzunar F5 490x490x360 (4 buc) pe afluent. 3) Sectiunea ventilatorului de alimentare ER63I-4DN.G7.1R L=14600 m3/ora, P=1912Pa; 4) Sectiunea recuperatorului rotativ eficienta energetica 82.1%; 5) Schimbator de caldura cu doua fete DR-HR.W-2.6-1240-900-2R-2-Cu0.4-AI0, 12-AISI304-2-Cu 12/18-E0-1-L-0 Qt=31.99 kW Qx=32.37 kW cu colector de picaturi si baie de scurgere condensat. 6) Sectiune de amortizor cu o legatura lunga de 2000 mm; 7) Sectiune multifunctionala cu amortizor actuator electric LM230A Belimo pe intrare; 8) Sectiune multifunctionala cu amortizor actuator electric LM230A Belimo pe capota; 9) Sectiunea prefiltrului Filtru MERV 8 pe hota; 10) Sectiunea MERV 14/15 pentru indepartarea plumbului praf, cu filtru de carbon pentru absorbtie gaze de praf de pusca, substante chimice si gaze si Filtru HEPA MERV 13 pe hota; 11) Sectiune de amortizor cu o legatura lunga de 2000 mm; 12) Sectiune ventilator cu evacuare ventilator ER71I-4DN.17.1R N=11 kW; 13) Carcasa externa pentru frecventa convertoare de tabla de otel cu ventilator si incalzire; 14) Unitate de automatizare VCS; 15) Panou de control HMITM; 16) Senzor de calitate a aerului; 17) Senzor de temperatura exterioara; 18) Senzor de temperatura interioara | Supply and exhaust unit 15/09 on intake and 15/12 on hood A+ left configuration with rotary heat recovery wheel and freon heat exchanger, thermal efficiency 82%, with filtration sections for a shooting range. Overall dimensions 8443x1560x2655. Automatic control system C5 complete set: L=14600 m3/h, P=1208/1517 Pa, complete set. 1) Multifunction section with electrically actuated damper LM230A Belimo with flexibility. 2) Filtration section with pocket filter F5 490x490x360 (4 pcs) on supply air. 3) Supply fan section ER63I-4DN.G7.1R L=14600 m3/h, P=1912 Pa; 4) Rotary heat recovery section energy efficiency 82.1%; 5) Double-sided heat exchanger DR-HR.W-2.6-1240-900-2R-2-Cu0.4-AI0, 12-AISI304-2-Cu 12/18-E0-1-L-0 Qt=31.99 kW Qx=32.37 kW with droplet separator and condensate drain pan; 6) Damper section with 2000 mm flexible connection; 7) Multifunction section with electric actuator damper LM230A Belimo at inlet; 8) Multifunction section with electric actuator damper LM230A Belimo at hood; 9) Prefilter section MERV 8 on hood; 10) Filtration section MERV 14/15 for removal of lead dust, with carbon filter for absorption of gunpowder gases, chemical substances and gases, and HEPA filter MERV 13 on hood; 11) Damper section with 2000 mm flexible connection; 12) Exhaust fan section ER71I-4DN.17.1R N=11 kW; 13) External housing for frequency converters made of steel sheet with ventilation and heating; 14) Automation unit VCS; 15) Control panel HMI; 16) Air quality sensor; 17) Outdoor temperature sensor; 18) Indoor temperature sensor.
10 | 2-1-4 | 134 | Unitate exterioara pentru schimbator de caldura cu doua fete Qx=80 kW, Qt=80 kW, N=20.61 kW. Temperatura aerului exterior la racire -15*C, incalzire la -20*C, Freon R32, A++. Dimensiuni totale: 2 bucati 1240x740x1858 cu suporturi antivibratii pentru unitate exterioara (8 buc), cadru pentru KKB 1270x740 inaltime 700mm (2 buc) tip KKB-PUHY-P700YSNW-A1 (PUHY-P350+PUHY-P350) sau analog | Outdoor unit for double-sided heat exchanger Qx=80 kW, Qt=80 kW, N=20.61 kW. Outdoor air temperature: cooling -15C, heating -20C. Refrigerant R32, A++. Overall dimensions: 2 units 1240x740x1858 with anti-vibration supports for outdoor unit (8 pcs), frame for KKB 1270x740 height 700 mm (2 pcs) type KKB-PUHY-P700YSNW-A1 (PUHY-P350+PUHY-P350) or equivalent.
11 | 2-1-4 | 135 | Unitate de admisie si evacuare 15/09 pe admisie si 15/12 pe capota A+ stanga cu actionare rotativa recuperator si schimbator de caldura cu freon, eficienta termica 82% cu sectiuni de filtrare pentru un poligon de tragere. Dimensiuni totale 8443x1560x2655 sistemul de control automat C5 in set complet: L=14600 m3/ora, P=1208/1517 Pa, set complet. 1) Sectiune multifunctionala cu amortizor actionare electrica LM230A Belimo cu flexibilitate. 2) Sectiune de filtrare cu filtru de buzunar M5 490x490x360 (4 buc) pe hota. 3) Sectiunea ventilatorului de alimentare ER63I-4DN.G7.1R L=14600 m3/ora, P=1912Pa; 4) Sectiunea recuperatorului rotativ eficienta energetica 82.1%; 5) Schimbator de caldura cu doua fete DR-HR.W-2.6-1240-900-2R-2-Cu0.4-AI0, 12-AISI304-2-Cu 12/18-E0-1-L-0 Qt=31.99 kW Qx=32.37 kW cu colector de picaturi si baie de scurgere condensat. 6) Sectiune de amortizor cu o legatura lunga de 2000 mm; 7) Sectiune multifunctionala cu amortizor actuator electric LM230A Belimo pe intrare; 8) Sectiune multifunctionala cu amortizor actuator electric LM230A Belimo pe capota; 9) Sectiunea prefiltrului Filtru MERV 8 pe hota; 10) Sectiunea MERV 14/15 pentru indepartarea plumbului praf, cu filtru de carbon pentru absorbtie gaze de praf de pusca, substante chimice si gaze si Filtru HEPA MERV 13 pe hota; 11) Sectiune de amortizor cu o legatura lunga de 2000 mm; 12) Sectiune ventilator cu evacuare ER71I-4DN.17.1R N=11 kW; 13) Carcasa externa pentru frecventa convertoare de tabla de otel cu ventilator si incalzire; 14) Unitate de automatizare VCS; 15) Panou de control HMITM; 16) Senzor de calitate a aerului; 17) Senzor de temperatura exterioara; 18) Senzor de temperatura interioara | Supply and exhaust unit 15/09 on intake and 15/12 on hood A+ left configuration with rotary heat recovery wheel and freon heat exchanger, thermal efficiency 82%, with filtration sections for a shooting range. Overall dimensions 8443x1560x2655. Automatic control system C5 complete set: L=14600 m3/h, P=1208/1517 Pa, complete set. 1) Multifunction section with electrically actuated damper LM230A Belimo with flexibility. 2) Filtration section with pocket filter M5 490x490x360 (4 pcs) on hood. 3) Supply fan section ER63I-4DN.G7.1R L=14600 m3/h, P=1912 Pa; 4) Rotary heat recovery section energy efficiency 82.1%; 5) Double-sided heat exchanger DR-HR.W-2.6-1240-900-2R-2-Cu0.4-AI0, 12-AISI304-2-Cu 12/18-E0-1-L-0 Qt=31.99 kW Qx=32.37 kW with droplet separator and condensate drain pan; 6) Damper section with 2000 mm flexible connection; 7) Multifunction section with electric actuator damper LM230A Belimo at inlet; 8) Multifunction section with electric actuator damper LM230A Belimo at hood; 9) Prefilter section MERV 8 on hood; 10) Filtration section MERV 14/15 for removal of lead dust, with carbon filter for absorption of gunpowder gases, chemical substances and gases, and HEPA filter MERV 13 on hood; 11) Damper section with 2000 mm flexible connection; 12) Exhaust fan section ER71I-4DN.17.1R N=11 kW; 13) External housing for frequency converters made of steel sheet with ventilation and heating; 14) Automation unit VCS; 15) Control panel HMI; 16) Air quality sensor; 17) Outdoor temperature sensor; 18) Indoor temperature sensor.
12 | 2-1-4 | 136 | Unitate exterioara pentru schimbator de caldura cu doua fete Qx=80 kW, Qt=80 kW, N=20.61 kW. Temperatura aerului exterior la racire -15*C, incalzire la -20*C, Freon R32, A++. Dimensiuni totale: 2 bucati 1240x740x1858 cu suporturi antivibratii pentru unitate exterioara (8 buc), cadru pentru KKB 1270x740 inaltime 700mm (2 buc) tip KKB-PUHY-P700YSNW-A1 (PUHY-P350+PUHY-P350) sau analog | Outdoor unit for double-sided heat exchanger Qx=80 kW, Qt=80 kW, N=20.61 kW. Outdoor air temperature: cooling -15°C, heating -20°C. Refrigerant R32, A++. Overall dimensions: 2 units 1240x740x1858 with anti-vibration supports for outdoor unit (8 pcs), frame for KKB 1270x740 height 700 mm (2 pcs) type KKB-PUHY-P700YSNW-A1 (PUHY-P350+PUHY-P350) or equivalent.
13 | 2-1-4 | 137 | Clapeta antifoc normal deschisa EI120 1350x500 | Normally open fire damper EI120 1350x500.
14 | 2-1-4 | 138 | Clapeta antifoc normal deschisa EI120 1300x500 | Normally open fire damper EI120 1300x500.
15 | 2-1-4 | 139 | Clapeta antifoc normal deschisa EI120 400x300 | Normally open fire damper EI120 400x300.
16 | 2-1-4 | 140 | Clapeta antifoc normal deschisa EI120 200x300 | Normally open fire damper EI120 200x300.
17 | 2-1-4 | 141 | Clapeta SRU 1400x510 cu servomotor electric BLE230 sau analog | Damper SRU 1400x510 with electric servomotor BLE230 or equivalent.
18 | 2-1-4 | 142 | Unitate interioara cu ionizator si biofiltru Qx=3.517 kW Qm=3.81 kW consum de aer 584-477-395 m3/ora, nivel de zgomot 21-39,5 dB, 802x189x297, greutate 8.6 kg ACP-12CH35AERI/I+ sau analog | Indoor unit with ionizer and biofilter Qx=3.517 kW Qm=3.81 kW, airflow 584-477-395 m3/h, noise level 21-39.5 dB, dimensions 802x189x297, weight 8.6 kg ACP-12CH35AERI/I+ or equivalent.
19 | 2-1-4 | 143 | Unitate exterioara R32 N=1.9 kW, nivel de zgomot 54dB, 890x342x673, 48 kg ACP-21COFM50AERI sau analog, cu suporturi antivibratii | Outdoor unit R32 N=1.9 kW, noise level 54 dB, dimensions 890x342x673, weight 48 kg ACP-21COFM50AERI or equivalent, with anti-vibration supports.
20 | 2-1-4 | 144 | Aparat de aer conditionat de perete Qx=6.1 kW Qm=7 kW, N=1.72 kW, functioneaza pentru incalzire pana la -20*C pentru temperaturi scazute pana la -15*C, cu suporturi antivibratii pentru unitatea exterioara tip PKA-M60KA(L)2 + PUHZ-ZRP60VHA2 sau analog | Wall-mounted air conditioner Qx=6.1 kW Qm=7 kW, N=1.72 kW, operates for heating down to -20C and for low ambient temperatures down to -15C, with anti-vibration supports for outdoor unit type PKA-M60KA(L)2 + PUHZ-ZRP60VHA2 or equivalent.
21 | 2-1-4 | 145 | Aparat de aer conditionat de perete Qx=2.7 kW Qm=3 kW, N=0.407 kW, functioneaza pentru incalzire pana la -20*C pentru temperaturi scazute pana la -15*C, cu suporturi antivibratii pentru unitatea exterioara tip CH-S09FTXLA2-NG + PUHZ-ZRP60VHA2 sau analog | Wall-mounted air conditioner Qx=2.7 kW Qm=3 kW, N=0.407 kW, operates for heating down to -20C and for low ambient temperatures down to -15C, with anti-vibration supports for outdoor unit type CH-S09FTXLA2-NG + PUHZ-ZRP60VHA2 or equivalent.
22 | 2-1-4 | 146 | Pompa de evacuare a condensului pentru aparate de aer conditionat cu o capacitate pina la 46 kW, consum de energie 21W, nivel de zgomot 19 V, inclusiv pompa MAXI BOX 230V 50Hz (sau analog), rezervor, capac rezervor cu cablu senzor 1.5 m lungime, rezervor submersibil, plutitor si filtru, lungimea tubului 220 mm cu interior diametru 6 mm, tub de admisie lung de 220 mm cu diametru interior 14 mm, tub de admisie a aerului lung de 150 mm cu diametru interior 6 mm, kit de conectare, set accesorii instalare | Condensate drain pump for air conditioners with capacity up to 46 kW, power consumption 21W, noise level 19 dB, including MAXI BOX pump 230V 50Hz (or equivalent), tank, tank cover with 1.5 m sensor cable, submersible reservoir, float and filter, discharge tube length 220 mm with internal diameter 6 mm, long inlet tube 220 mm with internal diameter 14 mm, air intake tube length 150 mm with internal diameter 6 mm, connection kit, installation accessories set.
|  |  | Retele telecomunicatii (12/25-J-TS) | Telecommunications networks (12/25-J-TS).
23 | 2-1-6 | 97 | Dulap pe perete 12U, 650x600x600 mm, 19", dezasamblat, usa din sticla (sarcina pina la 100 kg), p/u fixarea echipamentului 19", laterale sunt detasabile cu lacata, cu elementele de fixare incluse in set (Dulap IT 19", 12U (DT.1)) | Wall-mounted cabinet 12U, 650x600x600 mm, 19", disassembled, glass door (load up to 100 kg), for mounting 19" equipment, removable side panels with lock, fastening elements included in set (IT cabinet 19", 12U (DT.1)).
24 | 2-1-6 | 98 | Comutator de acces, cu 24 RJ-45 auto-negotiating 1 Gbps + min. 2 SFP+ 10 Gbps; min. 1 GB DDR3; 512 MB NAND flash, Throughput min. 95 Mpps; Switching capacity 128 Gbps; MAC address table size min. 32k; VLAN table min. 4K; QoS, SSL, RSTP, BPDU, LLDP, LACP, CLI, ACL, SNMP, DHCP-Snooping, IPv4 and IPv6 Management, Telnet/SSH; 19", 1U; P.el. = max. 80 W (de tip HPE Instant On Switch Series 1960 JL806A) sau analog | Access switch with 24 RJ-45 auto-negotiating 1 Gbps ports + minimum 2 SFP+ 10 Gbps; minimum 1 GB DDR3; 512 MB NAND flash; throughput minimum 95 Mpps; switching capacity 128 Gbps; MAC address table minimum 32k; VLAN table minimum 4K; QoS, SSL, RSTP, BPDU, LLDP, LACP, CLI, ACL, SNMP, DHCP-Snooping, IPv4 and IPv6 management, Telnet/SSH; 19", 1U; P.el. max. 80 W (type HPE Instant On Switch Series 1960 JL806A) or equivalent.
25 | 2-1-6 | 99 | Comutator de acces, cu 24 RJ-45 auto-negotiating 1 Gbps + min. 2 SFP+ 10 Gbps; min. 1 GB DDR3; 512 MB NAND flash, Throughput min. 95 Mpps; Switching capacity 128 Gbps; MAC address table size min. 32k; VLAN table min. 4K; QoS, SSL, RSTP, BPDU, LLDP, LACP, CLI, ACL, SNMP, DHCP-Snooping, IPv4 and IPv6 Management, Telnet/SSH; 19", 1U; P.el. = max. 480 W (de tip HPE Instant On Switch Series 1960 JL807A) sau analog | Access switch with 24 RJ-45 auto-negotiating 1 Gbps ports + minimum 2 SFP+ 10 Gbps; minimum 1 GB DDR3; 512 MB NAND flash; throughput minimum 95 Mpps; switching capacity 128 Gbps; MAC address table minimum 32k; VLAN table minimum 4K; QoS, SSL, RSTP, BPDU, LLDP, LACP, CLI, ACL, SNMP, DHCP-Snooping, IPv4 and IPv6 management, Telnet/SSH; 19", 1U; P.el. max. 480 W (type HPE Instant On Switch Series 1960 JL807A) or equivalent.
26 | 2-1-6 | 100 | Wi-Fi access point; wall and ceiling mount indoor; min. 1 x RJ-45 1 Gbps POE+ (802.3at); BLE Bluetooth; Integrated number of radios 2.4/5.0/6 GHz; aggregated wireless speed min 2.0 Gbps; built-in omni antennas 3.2 dBi for 2.4GHz, 5.3 dBi for 5 GHz; 6 dBi for 6 GHz; BSSID - 8 per radio; Standards 802.11/a/b/g/n/ac/ax; features DL/UL MU-MIMO (de tip Ubiquiti UniFi 6 Enterprise) sau analog | Wi-Fi access point; wall and ceiling indoor mounting; minimum 1 x RJ-45 1 Gbps PoE+ (802.3at); BLE Bluetooth; integrated radios 2.4/5.0/6 GHz; aggregated wireless speed minimum 2.0 Gbps; built-in omnidirectional antennas 3.2 dBi (2.4 GHz), 5.3 dBi (5 GHz), 6 dBi (6 GHz); BSSID 8 per radio; standards 802.11 a/b/g/n/ac/ax; supports DL/UL MU-MIMO (type Ubiquiti UniFi 6 Enterprise) or equivalent.
27 | 2-1-6 | 101 | PDU (Power distribution unit), 1U, 16A, 200-240V, 50/60Hz, Out-min. 4xCEE 7/3, In-UPS plug 1xIEC 14, montare orizontala pentru 19" rack, cu butonul de siguranta | PDU (Power Distribution Unit), 1U, 16A, 200-240V, 50/60Hz, outputs minimum 4xCEE 7/3, input UPS plug 1xIEC 14, horizontal mounting for 19" rack, with safety button.
28 | 2-1-6 | 102 | UPS 19", 1U, 1550VA/1100W, Length/Depth max. 560 mm, output min. 4xIEC C13 sockets, Single Phase 220V/230V/240V | UPS 19", 1U, 1550VA/1100W, maximum depth 560 mm, output minimum 4xIEC C13 sockets, single phase 220V/230V/240V.
29 | 2-1-6 | 111 | Camera video, min. 2560x1440 (4 MPx), 1/3" CMOS, IR=20m, 2.8 mm F2.2, 802.3 af Class 3, max 9 W (IPOX PX-DI4028IR2DLPW) sau analog | Video camera minimum 2560x1440 (4 MPx), 1/3" CMOS, IR=20m, 2.8 mm F2.2, 802.3af Class 3, maximum 9 W (IPOX PX-DI4028IR2DLPW) or equivalent.
30 | 2-1-6 | 112 | Camera video, min. 3200x1800 (6 MPx), 1/2.7" CMOS, IR=20m, 2.8 mm F1.6, 802.3 af Class 3, max 9 W (IPOX PX-TI6028IR2DL) sau analog | Video camera minimum 3200x1800 (6 MPx), 1/2.7" CMOS, IR=20m, 2.8 mm F1.6, 802.3af Class 3, maximum 9 W (IPOX PX-TI6028IR2DL) or equivalent.
31 | 2-1-6 | 113 | Registrator video, 32-ch, 2xSATA interfaces, H.265+, H.265, H.264+, H.264, 1x VGA, 2x HDMI (4K UHD/Full HD), 2xRJ45 10/100/1000Mbps, ONVIF, consumul de energie electrica max. 100W (IPOX PX-NVR3282H-L2) sau analog | Video recorder 32-channel, 2xSATA interfaces, H.265+, H.265, H.264+, H.264, 1xVGA, 2xHDMI (4K UHD/Full HD), 2xRJ45 10/100/1000 Mbps, ONVIF, maximum power consumption 100 W (IPOX PX-NVR3282H-L2) or equivalent.
32 | 2-1-6 | 114 | Hard disc pentru supraveghere video, 3.5", 20TB, 256M/SATA 6Gb/s/RV Sensor HDD 20TB | Surveillance hard disk 3.5", 20TB, 256M/SATA 6Gb/s/RV Sensor HDD 20TB.
33 | 2-1-6 | 115 | Controler pentru administrarea 1 usa (1 lacat electromagnetic/electromecanic) cu 2 cititori si cu 1 contact magnetic pe usa pentru monitorizare, RJ45, inclusiv sursa de alimentare 24 VDC/2.2A, in dulapul din metal de la producator tip Roger MC16-PAC-ST-1-KIT sau analog | Controller for management of 1 door (1 electromagnetic/electromechanical lock) with 2 readers and 1 magnetic door contact for monitoring, RJ45, including 24 VDC/2.2A power supply, installed in manufacturer metal cabinet type Roger MC16-PAC-ST-1-KIT or equivalent.
34 | 2-1-6 | 116 | Acumulator 17Ah | Battery 17Ah.
35 | 2-1-6 | 117 | Cititor pentru controlul accesului cu tastatura si cu cititor integrat de carduri fara contact (MIFARE Ultralight/Classic), RS485, IP65, compatibil cu controler de acces tip Roger MCT82M keypad sau analog | Access control reader with keypad and integrated contactless card reader (MIFARE Ultralight/Classic), RS485, IP65, compatible with Roger MCT82M keypad controller or equivalent.
36 | 2-1-6 | 119 | Lacat electromecanic, 12V/24 VDC, cu contact pentru monitorizarea tip ASSA ABLOY Trimec ES8000 V-Lock Motorised Bolt sau analog | Electromechanical lock 12V/24 VDC, with monitoring contact type ASSA ABLOY Trimec ES8000 V-Lock Motorised Bolt or equivalent.
37 | 2-1-6 | 120 | Amortizator cu brat articulat (door closer), pentru usa din metal cu greutate usa m=80 kg tip ASSA ABLOY DC270 sau analog | Door closer with articulated arm for metal door with door weight m=80 kg type ASSA ABLOY DC270 or equivalent.
38 | 2-1-6 | 140 | Amplificator IP pentru sistem de notificare 19" 2U 100V RJ45 TCP/IP UDP Pel=180 W tip ITC T-77240B sau analog | IP amplifier for notification system 19" 2U 100V RJ45 TCP/IP UDP Pel=180 W type ITC T-77240B or equivalent.
39 | 2-1-6 | 141 | Microfon IP pentru anuntarea comenzilor, RJ45 TCP/IP, UDP, IGMP (Multicast) DC24V/2A tip ITC T-7702A sau analog | IP microphone for voice announcements, RJ45 TCP/IP, UDP, IGMP (Multicast) DC24V/2A type ITC T-7702A or equivalent.
40 | 2-1-6 | 142 | Difuzor pentru instalare in sala de tragere, 6W, 100V tip ITC T-601 sau analog | Loudspeaker for installation in shooting range, 6W, 100V type ITC T-601 or equivalent.
|  |  | Semnalizarea de incendiu (12/25-J-SI) | Fire alarm system (12/25-J-SI).
41 | 2-1-7 | 43 | Panou de incendiu - centrala de detectie de incendiu cu 4 zone de securitatea, cu iesire pentru sirena si pentru transmitator radio, cu RIP (de tip SmartLine 036-04, INIM). In carcasa din metal, rosu, cu usa din sticla, cu cheie sau analog | Fire alarm control panel with 4 detection zones, siren output and radio transmitter output, with RIP (type SmartLine 036-04, INIM). In red metal enclosure with glass door, with key or equivalent.
42 | 2-1-7 | 49 | Transmitator radio, cu translarea min. 2 canale separate, LARS, LARS1, 1500 mA tip ATS-100 sau analog | Radio transmitter with transmission on minimum 2 separate channels, LARS, LARS1, 1500 mA type ATS-100 or equivalent.
43 | 2-1-7 | 57 | Senzor de aspiratie pentru monitorizarea mediului in canalul de ventilatie class C, cu 4 iesiri pentru programarea 4 evenimente filtru de aer in set tip INIM FA100 sau analog | Aspirating smoke detector for monitoring environment in ventilation duct class C, with 4 programmable events, air filter included in set type INIM FA100 or equivalent.
44 | 2-1-7 | 60 | Panou informativ pentru dublarea semnalelor tip SmartLetUSee/LCD-Lite repeaters sau analog | Repeater information panel for signal duplication type SmartLetUSee/LCD-Lite repeaters or equivalent.