ANNEX 2: QUOTATION SUBMISSION FORM
Bidders are requested to complete this form, including the Company Profile and Bidder’s Declaration, sign it and return it as part of their quotation along with Annex 3: Technical and Financial Offer. Bidders shall fill in this form in accordance with the instructions indicated. No alterations to its format shall be permitted and no substitutions shall be accepted. 
	Name of Bidder:
	Click or tap here to enter text.

	RFQ reference:
	RfQ26/03310: CBM/ Installation of photovoltaic system in Holercani, Dubasari
	Date: Click or tap to enter a date.


Company Profile
	Item Description
	Detail

	Legal name of bidder or Lead entity for JVs
	Click or tap here to enter text.

	Legal Address, City, Country
	Click or tap here to enter text.

	Website
	Click or tap here to enter text.

	Year of Registration
	Click or tap here to enter text.

	Legal structure
	Choose an item.

	Are you a UNGM registered vendor?
	☐ Yes ☐ No 







If yes, insert UNGM Vendor Number

	Quality Assurance Certification (e.g. ISO 9000 or Equivalent) (If yes, provide a Copy of the valid Certificate):
	☐ Yes ☐ No                    

	Does your Company hold any accreditation such as ISO 14001 or ISO 14064 or equivalent related to the environment? (If yes, provide a Copy of the valid Certificate):
	☐ Yes ☐ No

	Does your Company have a written Statement of its Environmental Policy? (If yes, provide a Copy)
	☐ Yes ☐ No

	Does your organization demonstrate significant commitment to sustainability through some other means, for example internal company policy documents on women empowerment, renewable energies or membership of trade institutions promoting such issues (If yes, provide a Copy)
	☐ Yes ☐ No


	Is your company a member of the UN Global Compact 
	☐ Yes ☐ No

	Bank Information
	Bank Name: Click or tap here to enter text.
Bank Address: Click or tap here to enter text.
IBAN: Click or tap here to enter text.
SWIFT/BIC: Click or tap here to enter text.
Account Currency: Click or tap here to enter text.
Bank Account Number: Click or tap here to enter text.

	Previous relevant experience: 
2 (two) successfully completed contracts of similar nature and complexity for provision of PVP services and corresponding installation services with a power not less than 80kW each, in over the past 5 (five) years

	Name of previous contracts
	Client & Reference Contact Details including e-mail
	Contract Value (insert currency)
	Period of activity
(month/year)
	Types of activities undertaken

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	


Bidder’s Declaration
	Yes
	No
	

	☐
	☐
	Requirements and Terms and Conditions: I/We have read and fully understand the RFQ, including the RFQ Information and Data, Schedule of Requirements, the General Conditions of Contract, and any Special Conditions of Contract. I/we confirm that the Bidder agrees to be bound by them.

	☐
	☐
	I/We confirm that the Bidder has the necessary capacity, capability, and necessary licenses to fully meet or exceed the Requirements and will be available to deliver throughout the relevant Contract period.

	☐
	☐
	Ethics: In submitting this Quote I/we warrant that the bidder: has not entered into any improper, illegal, collusive or anti-competitive arrangements with any Competitor; has not directly or indirectly approached any representative of the Buyer (other than the Point of Contact) to lobby or solicit information in relation to the RFQ ;has not attempted to influence, or provide any form of personal inducement, reward or benefit to any representative of the Buyer. 

	☐
	☐
	I/We confirm to undertake not to engage in proscribed practices, , or any other unethical practice, with the UN or any other party, and to conduct business in a manner that averts any financial, operational, reputational or other undue risk to the UN and we have read the United Nations Supplier Code of Conduct:https://www.un.org/Depts/ptd/about-us/un-supplier-code-conduct and acknowledge that it provides the minimum standards expected of suppliers to the UN.

	☐
	☐
	Conflict of interest: I/We warrant that the bidder has no actual, potential, or perceived Conflict of Interest in submitting this Quote or entering a Contract to deliver the Requirements. Where a Conflict of Interest arises during the RFQ process the bidder will report it immediately to the Procuring Organisation’s Point of Contact.

	☐
	☐
	Prohibitions and Sanctions: l/We hereby declare that our firm, ultimate beneficial owners, affiliates or subsidiaries or employees, including any JV/Consortium members or subcontractors or suppliers for any part of the contract is not under procurement prohibition by the United Nations, including but not limited to prohibitions derived from the Compendium of United Nations Security Council Sanctions Lists and have not been suspended, debarred, sanctioned or otherwise identified as ineligible by any UN Organization or the World Bank Group or any other international Organization.

	☐
	☐
	Bankruptcy: l/We have not declared bankruptcy, are not involved in bankruptcy or receivership proceedings, and there is no judgment or pending legal action against them that could impair their operations in the foreseeable future.

	☐
	☐
	Offer Validity Period: I/We confirm that this Quote, including the price, remains open for acceptance for the Offer Validity.  

	☐
	☐
	I/We understand and recognize that you are not bound to accept any Quotation you receive, and we certify that the goods offered in our Quotation are new and unused.

	☐
	☐
	By signing this declaration, the signatory below represents, warrants and agrees that he/she has been authorised by the Organization/s to make this declaration on its/their behalf.


Signature: 

Name: 
Click or tap here to enter text.
Title:
Click or tap here to enter text.
Date:  
Click or tap to enter a date.

ANNEX 3: TECHNICAL AND FINANCIAL OFFER – WORKS

Bidders are requested to complete this form, sign it and return it as part of their quotation along with Annex 2 Quotation Submission Form. The Bidder shall fill in this form in accordance with the instructions indicated. No alterations to its format shall be permitted and no substitutions shall be accepted.
	Name of Bidder:
	Click or tap here to enter text.

	RFQ reference:
	RfQ26/03310: CBM/ Installation of photovoltaic system in Holercani, Dubasari
	Date: Click or tap to enter a date.


Technical Offer
Provide the following:
- a brief description of company’s qualifications and capacity that is relevant to the Scope of Works;

- a brief method statement and implementation plan;

- team composition and CVs of key personnel.

Financial Offer
Currency of the Quotation: Moldovan Leu (MDL) for local companies and US Dollars (USD) for international companies
	BOQ Chapter
	Description of Works
	Total Price (VAT 0%) (insert currency) 

	2-1-1
	Photovoltaic Module. Electrical Networks
	

	2-1-2
	Separate connection. Electrical Networks
	

	2-1-3
	Photovoltaic Installation. Construction Works
	

	
	Cost of insurances: Insurance of works, Liability insurance
	

	
	Other costs if any (pls. specify)
	

	
	TOTAL and All-inclusive PRICE (VAT 0%) [Please insert currency]
	


Compliance with Requirements

	Requirements
	You Responses

	
	Yes, we will comply
	No, we cannot comply
	If you cannot comply, pls. indicate counter - offer

	Delivery Lead Time – 90 days
	☐
	☐
	Click or tap here to enter text.

	Validity of Quotation – 90 days
	☐
	☐
	Click or tap here to enter text.

	Payment terms
	☐
	☐
	Click or tap here to enter text.

	Installation Requirements

All the works must be carried out in accordance with national/local standards regarding civil works
	☐
	☐
	Click or tap here to enter text.

	Testing Requirements

Done by Contractor according to SM EN IEC 62446-2:2020 – Photovoltaic systems. Requirements for testing, documentation and maintenance
	☐
	☐
	Click or tap here to enter text.

	Training in Operation and Maintenance

Done by Contractor at the premises of the beneficiary.
	☐
	☐
	Click or tap here to enter text.

	Commissioning
Commissioning of the works must be initiated by the Supplier:
· Laboratory tests performing.

· Hand-over documentation and technical acceptance by the energy authority and network operator.
· Commissioning at the end of the works.

· Final commissioning after 1-year warranty period
	☐
	☐
	Click or tap here to enter text.

	Minimum warranty provided:

· General warranty: ≥ 5 years for the entire PV system

· Panel yield warranty: ≥ 10 years (min. 80% performance)

· Inverter and electricity meter warranty: ≥ 5 years
	☐
	☐
	Click or tap here to enter text.

	List of transportation and specialized equipment units to be confirmed with the rights of ownership or contract of lease and availability of the functioning permit in line with national legislation
	☐
	☐
	Click or tap here to enter text.

	Technical Support Requirements
The contracted company will provide on-site support within 10 days from the moment of beneficiary’s notification.
The turnaround time for answering queries will be less than 3 days.
	☐
	☐
	Click or tap here to enter text.

	After-sale services Requirements

Provided by Contractor according to ANNEX 1: SCHEDULE OF REQUIREMENTS
	☐
	☐
	Click or tap here to enter text.

	Local Service Support

The Contractor must provide a list of at least one authorized representative located in Moldova.
	☐
	☐
	Click or tap here to enter text.

	All Provisions of the UNDP General Terms and Conditions accepted
	☐
	☐
	Click or tap here to enter text.


	I, the undersigned, certify that I am duly authorized to sign this quotation and bind the company below in event that the quotation is accepted.

	Exact name and address of company

Company NameClick or tap here to enter text.
Address: Click or tap here to enter text.




Phone No.: Click or tap here to enter text.



Email Address:
Click or tap here to enter text.
	Authorized Signature: 









Date: Click or tap here to enter text.





Name: Click or tap here to enter text.




Functional Title of Authorised Signatory: Click or tap here to enter text.



Email Address: Click or tap here to enter text.



ANNEX 4: TECHNICAL RESPONSIVENESS TABLE
Bidders are requested to complete this form, sign it and return it as part of their quotation along with Annex 2 Quotation Submission Form. The Bidder shall fill in this form in accordance with the instructions indicated. No alterations to its format shall be permitted and no substitutions shall be accepted.

	Name of Bidder:
	Click or tap here to enter text.

	RFQ reference:
	RfQ26/03310: Installation of photovoltaic system in Holercani, Dubasari
	Date: Click or tap to enter a date.


Bidders shall provide all the applicable technical data of the materials proposed to demonstrate compliance with technical specifications included in Section 5: Schedule of Requirements; failing to do so may result in the bid being rejected. Corresponding documentation shall form part of the bidder’s offer. You may also provide brochures for the offered equipment; in case it is available.
	No.
	Technical parameters/characteristics for proposed materials
	Requested characteristics
	Quantity, pcs
	Bidder’s response

	
	
	
	
	Compliance with technical specifications
	Technical Compliance

(indicate details of proposed materials)

	
	
	
	
	Yes, we comply
	No, we cannot comply

(indicate discrepancies)
	

	

	Three Phase Hybrid Inverter
	Quantity – 1 pc

	1
	Battery Input Data
	
	
	
	
	

	
	Battery Type
	Lithium-ion
	
	
	
	

	
	Battery Voltage Range (V)
	160-1000
	
	
	
	

	
	Max. Charging Current (A)
	80+80
	
	
	
	

	
	Max. Discharging Current (A)
	80+80
	
	
	
	

	
	Charging Strategy for Li-ion Battery
	Self-adaption to BMS
	
	
	
	

	
	Number of Battery Input
	2
	
	
	
	

	2
	PV String Input Data
	
	
	
	
	

	
	Max. PV Access Power (W)
	160000
	
	
	
	

	
	Max. PV Input Power (W)
	128000
	
	
	
	

	
	Max. PV Input Voltage (V)
	1000
	
	
	
	

	
	Start-up Voltage (V)
	180
	
	
	
	

	
	MPPT Voltage Range (V)
	150-850
	
	
	
	

	
	Rated PV Input Voltage (V)
	650
	
	
	
	

	
	Max. Operating PV Input Current (A)
	36+36+36+36+36+36
	
	
	
	

	
	Max. Input Short-Circuit Current (A)
	54+54+54+54+54+54
	
	
	
	

	
	No. of MPP Trackers/ No. of Strings MPP Tracker
	6/2+2+2+2+2+2
	
	
	
	

	3
	AC Input/Output Data
	
	
	
	
	

	
	Rated AC Input/Output Active Power (W)
	80000
	
	
	
	

	
	Max. AC Input/Output Apparent Power (VA
	88000
	
	
	
	

	
	Rated AC Input/Output Current (A)
	121.3/115.9
	
	
	
	

	
	Max. AC Input/Output Current (A)
	133.4/127.6
	
	
	
	

	
	Max. Continuous AC Passthrough (grid to load) (A)
	200
	
	
	
	

	
	Peak Power (off-grid) (W)
	1.5 times of rated power, 10s
	
	
	
	

	
	Power Factor Adjustment Range
	0.8 leading to 0.8 lagging
	
	
	
	

	
	Rated Input/Output Voltage/Range (V)
	220/380V, 230/400V 0.85Un-1.1Un
	
	
	
	

	
	Rated Input/Output Grid Frequency/Range(Hz)
	50/45-55, 60/55-65
	
	
	
	

	
	Grid Connection Form
	3L+N+PE
	
	
	
	

	
	Total Current Harmonic Distortion THDi
	<3% (of nominal power)
	
	
	
	

	
	DC Injection Current
	<0.5% In
	
	
	
	

	4
	Efficiency
	
	
	
	
	

	
	Max. Efficiency
	97.60%
	
	
	
	

	
	Euro Efficiency
	97.0%
	
	
	
	

	
	MPPT Efficiency
	>99%
	
	
	
	

	5
	Equipment Protection
	
	
	
	
	

	
	Protection
	manufacturer-provided
	
	
	
	

	
	Surge Protection Level
	TYPE II(DC), TYPE II(AC)
	
	
	
	

	6
	Interface
	
	
	
	
	

	
	Communication Interface
	RS485/RS232/CAN
	
	
	
	

	
	Monitor Mode
	GPRS/WIFI/Bluetooth/ 4G/LAN(optional)
	
	
	
	

	7
	General Data
	
	
	
	
	

	
	Operating Temperature Range (℃)
	-40 to +60°C, >45°C Derating
	
	
	
	

	
	Permissible Ambient Humidity
	0-100%
	
	
	
	

	
	Permissible Altitude
	3000 m
	
	
	
	

	
	Noise (dB)
	≤65
	
	
	
	

	
	Ingress Protection(IP) Rating
	IP 65
	
	
	
	

	
	Inverter Topology
	Non-Isolated
	
	
	
	

	
	Over Voltage Category
	OVC II(DC), OVC III(AC)
	
	
	
	

	
	Grid Regulation
	IEC 61727, IEC 62116, CEI 0-21, EN 50549, NRS 097, RD 140, UNE 217002, OVE-Richtlinie R25, G99, VDE-AR-N 4105
	
	
	
	

	
	Safety / EMC Standard
	IEC/EN 61000-6-1/2/3/4, IEC/EN 62109-1, IEC/EN 62109-2
	
	
	
	

	
	Warranty
	Minimum 5 Years
	
	
	
	

	N-type TOPCon Bifacial Dual-Glass Module
	Quantity – 120 pcs

	1
	General Ratings
	
	
	
	
	

	
	Power Output
	Minimum 700W
	
	
	
	

	
	Efficiency
	Minimum 23%
	
	
	
	

	
	Operational Temperature
	-40°C - +85°C
	
	
	
	

	
	Maximum System Voltage
	1500V DC
	
	
	
	

	2
	Mechanical Data
	
	
	
	
	

	
	Cell Type
	N-type TOPCon Monocrystalline
	
	
	
	

	
	Cell Count
	132
	
	
	
	

	
	Front Glass
	1.6 – 2.0 mm
	
	
	
	

	
	Back Glass
	1.6 – 2.0 mm
	
	
	
	

	
	Frame
	Anodized Aluminum Alloy
	
	
	
	

	
	Junction Box
	IP 68 rated
	
	
	
	

	
	Connector
	MC4 Compatible
	
	
	
	

	
	Cable
	Minimum 4 mm², minimum 1000V, direct current
	
	
	
	

	
	Certifications
	IEC61215 / IEC61730 / UL61730 / ISO9001 / ISO14001 / ISO45001 / IEC62941
	
	
	
	

	
	Snow Load
	Minimum 350 kg/m2
	
	
	
	

	
	Warranty
	Minimum 10 Years
	
	
	
	

	Electricity meter (System operator-approved)
	Quantity – 1 pc

	1
	Electrical Parameters
	
	
	
	
	

	
	Connection Type
	Indirect connection via Current Transformers (CT)
	
	
	
	

	
	Nominal Voltage (U n)
	3 × 220/380 V up to 3 × 230/400 V
	
	
	
	

	
	Voltage Tolerance
	-20% to +15% U n
	
	
	
	

	
	Nominal Current (I n / I ref)
	5 A
	
	
	
	

	2
	Accuracy & Measurement Classes
	
	
	
	
	

	
	Active/Reactive Energy (Bidirectional - Import/Export)
	Class 0.5 – 1.0 (IEC 62053-22, IEC 62053-21)
	
	
	
	

	
	Measured Parameters
	Active power, reactive power, apparent power, voltage (U), current (I), frequency (f), power factor (\(\cos \phi\)), total harmonic distortion (THD)
	
	
	
	

	3
	Communication & Modem Modules
	
	
	
	
	

	
	Integrated Modem Type
	4G LTE / 3G / GSM/GPRS or NB-IoT / LTE-M (with fallback to 2G) for remote automated meter reading (AMR)
	
	
	
	

	
	Local Interface Built-in
	RS-485 serial port and an Optical IR port (IEC 62056-21) for local readouts
	
	
	
	

	
	Supported Protocols
	DLMS/COSEM, Modbus RTU, or IEC 870-5-102
	
	
	
	

	
	Data Transmission Features
	Automatic Scheduled Meter Reading (AMR/AMI), remote configuration, event/alarm push notifications (tampering, power outages)
	
	
	
	

	
	Antenna Connection
	External SMA connector for high-gain signal antenna
	
	
	
	

	4
	Mechanical & Environmental Specifications
	
	
	
	
	

	
	Enclosure / Mounting
	DIN-rail (standard 35mm) or 3-point wall mounting pattern conforming to DIN 43859
	
	
	
	

	
	Ingress Protection Rating
	IP54 minimum (front-facing dust and splash protection)
	
	
	
	

	
	Operating Temperature
	-40°C to +70°C
	
	
	
	

	
	Relative Humidity Limit
	≤ 95% non-condensing
	
	
	
	

	
	Meter cabinet
	In accordance with the connection permit and execution project
	
	
	
	

	
	Warranty
	Minimum 5 Years
	
	
	
	

	
	
	
	
	
	
	





15

