## Arhitectural solutions
No. | Type of equipment requested by BoQ and its data | Bidder’s response
|  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  | Yes, we comply | No, we do not comply (indicate discrepancies)
ItB-26/03305: “Construction of the Administrative building for the provision of social services, with a height regime of S+G+3F, on land with cadastral number 1701115.673, Cahul municipality, loan Voda cel Cumplit street”
1 | Ventilated facade system with: - ceramic granite slab cladding 1200 x 2780 x 6.0 mm, with visible fixing with complete structures and fixing elements under the ventilated facade cladding (consoles, supporting profiles, anchors, clips, etc.), average specific weight: ≈ 14.5 - 15.0 kg/m², water absorption: ≤ 0.1%, bending strength: ≥ 35 N/mm² (ISO10545-4 standard); - mineral wool slabs with heat transfer coefficient 0.0362 W/m*K, water absorption (short-term) no more than 1.0 kg/m2, with density 90 kg/m3, thickness 150 mm BIANCO color
2 | Ventilated facade system made of RAL7021 composite panels, with hidden fastening, fire resistance of composite panels - min. A2/S1/d0, according to EN13501, thickness of panels min. 4.0 mm, thickness of foil - min. 0.5 mm on both sides. The load-bearing structure will be made of aluminum alloy profiles with their fastening with corrosion-resistant elements
3 | Blind interior door, fire resistant EI 30 with thermo-expandable gaskets, metal elements - galvanized, door leaf - 60 mm thick metal, painted in RAL9010 electrostatic field with mineral wool filling, door frame - corner metal, painted in RAL9010 electrostatic field, equipped with - 2 two hinges per leaf, one of which with bearing for vertical adjustment of the leaf, according to the EN 1935 standard, classified up to a weight of 160 kg, 200,000 cycles, used for fire doors and a spring hinge for self-closing, black fire-resistant nylon handles with steel insert, lock, cylinder
4 | Interior door frame made of MDF, HPL finish, RAL9010, with 1 full panel with stabilized honeycomb filling, equipped with frame extension, door frame (interior / exterior), deadbolts, Yalle lock and latch and 3 hinges per leaf
5 | Interior partition wall made of RAL 7024 aluminum profile, with 1-chamber double glazing, made of fixed panels and door leaves
6 | Exterior door in two leaves, made of RAL9010 aluminum profile, double-glazed glass 6FSG + 6 flat + 6 low-E EGS, with permanent opening in a single leaf (second leaf blocked), with anti-panic bar on both leaves, threshold with maximum height 20 mm, heat transfer coefficient Uw 1.90 W(m2*K)
7 | Window block made of RAL 7024 aluminum profiles, with fixed sashes, insulated glass pane 6FSG + 6 flat + 6 low-E EGS mm, overall heat transfer coefficient Uw 1.55 W(m2*K)

## Elevator
No. | Type of equipment requested by BoQ and its data | Bidder’s response
|  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  | Yes, we comply | No, we do not comply (indicate discrepancies)
ItB-26/03305: “Construction of the Administrative building for the provision of social services, with a height regime of S+G+3F, on land with cadastral number 1701115.673, Cahul municipality, loan Voda cel Cumplit street”
1 | Passenger elevator, certified energy consumption min class A +, load capacity min 630 kg, speed approx. 1.0 m/s, shaft size in which the elevator is installed 2200x2150 mm, number of stops - 5, number of doors - 5, door size 900x2000(h) mm, cabin lift height - 14.8 m - Application in the interior control panel and on levels with facilities for the blind and disabled; - Cabin doors 900x2000 mm made of satin stainless steel, fire resistance class EI 60; - Interior cabin - satin stainless steel, automatic opening in side stations with two panels, curtain-type obstacle protection over the entire height and width of the door; - Control panel with microcontroller in satin stainless steel mirror finish, collective system down, white lighting button that turns red when the command is recognized, white glass panel with LED MATRIX display, easy to read high resolution, status indicator with symbols, stainless steel interior cabin handrail with round ends, min diameter 40 mm, blind facilities; - Satin stainless steel cabin ceiling, evacuation hatch in the ceiling; - Bidirectional communication system, alarm device by telephone; - Automatic passenger evacuation system in case of power failure; - Landing indicators and landing control box mounted externally on the wall, touch buttons, aluminum cabin door threshold, aluminum landing door threshold; - Cabin interior floor - PVC carpet - resistant to at least 10,000 repeated passes with a chair or stretcher on wheels - certified by the Ministry of Health; - Cabin ventilation fan with circulated air flow; - Automatic cabin lighting (ON/OF) with LED, elevator shaft lighting; - Load verification system - electronic scale; - Elevator installation project.

## IVC
No. | Type of equipment requested by BoQ and its data | Bidder’s response
|  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  | Yes, we comply | No, we do not comply (indicate discrepancies)
ItB-26/03305: “Construction of the Administrative building for the provision of social services, with a height regime of S+G+3F, on land with cadastral number 1701115.673, Cahul municipality, loan Voda cel Cumplit street”
1 | PV_1. Suction/discharge installation in galvanized steel casing, thermally and acoustically insulated, EUROVENT- A+ certified, with 1 working fan reservation + 1 reserve on each line, La/r = 6500 / 6500 m3/h, Pa/r = 500 / 500 Pa, valves on suction and discharge lines, sealing class 2 according to EN1751:2003, with AC/DC 24V, 10Nm actuator, rotor type heat recovery 380V, 85 Hz, 0.62 A with 83.5% efficiency and control pressure gauge, filters on suction and discharge lines, bag type class M5 / M5 with control pressure gauge, 2-circuit freon-based heat exchanger, Qt/r ​​freon=27.0 / 56.3 kW, with stainless steel condensate collection and evacuation tray 1.4301 equipped with ball trap -1300Pa / +500Pa, outdoor location, with automation (frequency converter 0.37 kW, 3x380-480 V, IP20; cover with Nema Type 1 kit terminals, M1 0.37-0.75 kW; LCP 11 panel without potentiometer, mounting housing IP54 / IP20; free programming machine (controller) used for the automation of HVAC systems of the Climatix C600 series with configuration - 3 UI + 8 UIO + 4 DI + 6 DO with integrated communication interfaces: Ethernet, RS485, KNX, USB port for maintenance and SD card slot, supported protocols: Modbus (RTU/IP), BACnet (MS/TP or IP), PL-Link, JSON and OPC UA, equipped with integrated display (HMI), automatic program provision, passive room temperature sensor measuring range: 0 ... +50*C with 10 kOhm sensitive element; Climatix POL871.71/STD module - advanced portable operating interface HMI-TM)
2 | P_2. Discharge installation in galvanized steel casing, thermally and acoustically insulated, EUROVENT-A+ certified, with 2 discharge lines, with 1 working fan reservation + 1 reserve on each line, Lr = 1000 m3/h, Pr = 250 Pa, valves on suction lines, sealing class 2 according to EN1751:2003, with AC/DC 24V, 3Nm actuator, class G4 bag filter on suction lines with control pressure gauge, electric air heater N=5.40 kW, 380 V, 1-circuit freon-based heat exchanger, Qt/r ​​freon= 11.7 / 7.5 kW with a tray for collecting and discharging condensate made of stainless steel 1.4301 equipped with a ball siphon -1300Pa / +500Pa, indoor location, with automation (frequency converter 1.50 kW, 3x380-480 V, IP20 - 2 pcs; Nema Type 1 terminal covers kit, M1 1.50-2.20 kW - 2 pcs)
3 | Centrifugal duct fan, energy class - C, designed for round duct systems with D=160 mm, galvanized steel housing protected against corrosion, impeller with backward curved blades, AC motor, IP44, 230V, 50 Hz, 2480 rpm, N=0.108 kW, flow rate up to 767 m3/h (setting 112 m3/h), 200 Pa, noise level 43-49 dB(A) / 3 meters, with speed control via integrated potentiometer
4 | Centrifugal duct fan, energy class - B, designed for round duct systems with D=250 mm, ABS plastic housing, forced impeller, with backward curved blades, EC motor, IP44, 230V, 50 Hz, 2600 rpm, N=0.165 kW, flow rate up to 1250 m3/h (setting 450 m3/h), 200 Pa, noise level 48 dB(A) / 3 meters, with speed control via an integrated external 0-10 V signal
5 | Centrifugal duct fan, ErP Compliant marked, designed for round duct systems with D=560 mm, corrosion-resistant steel housing, centrifugal impeller with backward curved blades, AC motor, Class IE3, active TEFC cooling, IP55, 380V / 660V, 50 Hz, 1500 rpm, N=4.00 kW, flow rate up to 13000 m3/h (setting 10000 m3/h), 500 Pa, noise level 85 dB(A) / 3 meters, with speed control via integrated potentiometer
6 | Inverter type outdoor unit, intended for air conditioning systems. Dimensions min 950 x 1500 x 350 mm. Un=380 V AC, 50 Hz. Electricity consumption: - Cooling max 9.15 kW; - Heating max 9.12 kW. EER / COP - 2.95 / 3.29. Nominal cooling power of 27.0 kW (6.90...31.50 kW). Nominal heating power of 30.0 kW (6.90...33.5 kW). Sound pressure level: - Cooling max 75 dB (A); - Heating max 77 dB (A). Air flow: - Cooling min 136 m3/min; - Heating min 140 m3/min. Maximum pipe length - 60 m. Maximum level difference - above - 50 m / below - 15 m. Net weight - max 155.0 kg. Fasteners in set with vibration isolators. Refrigerant pipe connection size - 1 pc x 12.7 mm (1/2") / 1 pc x22.2 mm (7/8"). Refrigerant - Freon R32 with factory charge min 5.6 kg
7 | Multiple outdoor unit, designed for multi-split air conditioning systems. Max dimensions 945 x 970 x 370 mm. Un=230 V AC, 50 Hz. Power consumption: - Cooling 2.70 kW (0.48...3.65 kW); - Heating 2.38 kW (0.37...2.0 kW). EER / COP - 3.70 / 4.41. Nominal cooling power 10.0 kW (1.7...11.5 kW). Nominal heating power 10.5 kW (0.9...11.5 kW). Sound pressure level: - Cooling 54 dB (A); - Heating 59 dB (A). Air flow: - Cooling 75 m3/min; - Heating 75 m3/min. Maximum pipe length - 30 m. Net weight - 73.0 kg. Fasteners in the set. Refrigerant pipe connection size - 5 pcs x 6.35 mm (1/4") / 5 pcs x 9.52 mm (3/8"). Refrigerant - Freon R32 with factory charge min. 2.98 kg.
8 | Multiple outdoor unit, designed for multi-split air conditioning systems. Max dimensions 945 x 970 x 370 mm. Un=230 V AC, 50 Hz. Power consumption: - Cooling 3.90 kW (0.65...4.80 kW); - Heating 3.25 kW (0.70...3.42 kW). EER / COP - 3.21 / 4.15. Nominal cooling power 12.5 kW (1.8...14.0 kW). Nominal heating power 13.5 kW (1.5...14.0 kW). Sound pressure level: - Cooling 57 dB (A); - Heating 60 dB (A). Air flow: - Cooling 75 m3/min; - Heating 82 m3/min. Maximum pipe length - 30 m. Net weight - 92.0 kg. Fasteners in the set. Refrigerant pipe connection size - 6 pcs x 6.35 mm (1/4") / 6 pcs x 9.52 mm (3/8"). Refrigerant - Freon R32 with factory charge min. 6.0 kg
9 | Multiple outdoor unit, designed for multi-split air conditioning systems. Max dimensions 640 x 850 x 290 mm. Un=230 V AC, 50 Hz. Power consumption: - Cooling 1.32 kW (0.43...2.28 kW); - Heating 1.40 kW (0.32...2.80 kW). EER / COP - 4.55 / 4.86. Nominal cooling power 6.0 kW (1.6...7.5 kW). Nominal heating power 6.8 kW (1.0...7.50 kW). Sound pressure level: - Cooling 50 dB (A); - Heating 52 dB (A). Air flow: - Cooling 50 m3/min; - Heating 52 m3/min. Maximum pipe length - 30 m. Net weight - 48.5 kg. Fasteners in the set. Refrigerant pipe connection size - 3 pcs x 6.35 mm (1/4") / 3 pcs x 9.52 mm (3/8"). Refrigerant - Freon R32 with factory charge min. 1.8 kg.
10 | Multiple outdoor unit, designed for multi-split air conditioning systems. Max dimensions 595 x 780 x 290 mm. Un=230 V AC, 50 Hz. Power consumption: - Cooling 0.52 kW (0.32...1.60 kW); - Heating 0.74 kW (0.25...1.49 kW). EER / COP - 8.60 / 4.80. Nominal cooling power 3.0 kW (1.4...5.0 kW). Nominal heating power 4.0 kW (1.0...5.70 kW). Sound pressure level: - Cooling 49 dB (A); - Heating 51 dB (A). Air flow: - Cooling 32.5 m3/min; - Heating 32.5 m3/min. Maximum pipe length - 30 m. Net weight - 35.5 kg. Fasteners in the set. Refrigerant pipe connection size - 2 pcs x 6.35 mm (1/4") / 2 pcs x 9.52 mm (3/8"). Refrigerant - Freon R32 with factory charge min. 1.25 kg
11 | Wall-mounted indoor unit, designed for multi-split air conditioning systems. Dimensions max 305 x 920 x 220 mm. Un=230 V AC, 50 Hz. Nominal cooling power min 2.5 kW. Nominal heating power min 3.2 kW. It has 4 fan speed levels and includes air filter. Sound pressure level: - Cooling (39 / 33 / 25 / 19 dB (A)); - Heating (40 / 34 / 27 / 19 dB (A)). Total sound power: Cooling - max 55 dB(A); Heating - max 56 dB(A). Air flow: - Cooling (11.3 / 9.1 / 6.0 / 5.0 m3/min); - Heating (12.2 / 10.3 / 7.2 / 5.4 m3/min). Pipe connections: 1 pc x 6.35 mm (1/4") / 1 pc x 9.52 mm (3/8"). Weight - max 13.0 kg. Infrared remote control and fixing elements in the set. Refrigerant - Freon R32. 3D Auto System (for air distribution) Allergen Clear System, Washable Deodorizing Filter, Self-Clean Function, Eco Sensor (Human Sensor), Integrated Wi-Fi
12 | Wall-mounted indoor unit - split, designed for multi-split air conditioning systems. Max dimensions 305 x 920 x 220 mm. Un=230 V AC, 50 Hz. Nominal cooling power min 3.5 kW. Nominal heating power min 4.3 kW. It has 4 fan speed levels and includes air filter. Sound pressure level: - Cooling (43 / 35 / 26 / 19 dB (A)); - Heating (42 / 35 / 28 / 19 dB (A)). . Total sound power: Cooling - max 58 dB(A); Heating - max 58 dB(A). Air flow: - Cooling (13.1 / 10.8 / 7.3 / 5.0 m3/min); - Heating (13.9 / 11.8 / 8.6 / 5.4 m3/min). Pipe connections: 1 pc x 6.35 mm (1/4") / 1 pc x 9.52 mm (3/8"). Weight - max 13.0 kg. Infrared remote control and fixing elements in the set. Refrigerant - Freon R32. 3D Auto System (for air distribution) Allergen Clear System, Washable Deodorizing Filter, Self-Clean Function, Eco Sensor (Human Sensor), Integrated Wi-Fi
13 | Wall-mounted indoor unit - split, designed for multi-split air conditioning systems. Max dimensions 305 x 920 x 220 mm. Un=230 V AC, 50 Hz. Nominal cooling power min 6.1 kW. Nominal heating power min 6.8 kW. It has 4 fan speed levels and includes an air filter. Sound pressure level: - Cooling (48 / 41 / 33 / 22 dB (A)); - Heating (47 / 42 / 34 / 23 dB (A)). Total sound power: Cooling - max 62 dB(A); Heating - max 63 dB(A). Air flow: - Cooling (16.3 / 13.2 / 11.0 / 7.0 m3/min); - Heating (17.8 / 14.4 / 12.5 / 8.5 m3/min). Pipe connections: 1 pc x 6.35 mm (1/4") / 1 pc x 9.52 mm (3/8"). Weight - max 13.0 kg. Infrared remote control and fixing elements in the set. Refrigerant - Freon R32. 3D Auto System (for air distribution) Allergen Clear System, Washable Deodorizing Filter, Self-Clean Function, Eco Sensor (Human Sensor), Integrated Wi-Fi
14 | Ultra slim duct type indoor unit, designed for multi-split air conditioning systems. Max dimensions 200 x 750 x 500 mm. Un=230 V AC, 50 Hz. Nominal cooling power min 2.5 kW. Nominal heating power min 3.4 kW. It has 4 fan speed levels and includes air filter. Sound pressure level: - Cooling (37 / 33 / 30 / 24 dB (A)); - Heating (40 / 37 / 34 / 28 dB (A)). Total sound power: Cooling - max 56 dB(A); Heating - max 59 dB(A). Air flow: - Cooling (9.5 / 8.5 / 6.5 / 4.5 m3/min); - Heating (10.0 / 9.0 / 8.0 / 6.0 m3/min). Pipe connections: 1 pc x 6.35 mm (1/4") / 1 pc x 9.52 mm (3/8"). Weight - max 20.5 kg. Infrared remote control and fixing elements in the set. Refrigerant - Freon R32. Integrated condensate pump
15 | Ultra slim duct type indoor unit for multi-split air conditioning systems. Max dimensions 200 x 950 x 500 mm. Un=230 V AC, 50 Hz. Nominal cooling power min 5.0 kW. Nominal heating power min 5.8 kW. It has 4 fan speed levels and includes an air filter. Sound pressure level: - Cooling (41 / 37 / 34 / 29 dB (A)); - Heating (43 / 39 / 37 / 32 dB (A)). Total sound power: Cooling - max 58 dB(A); Heating - max 61 dB(A). Air flow: - Cooling (13.5 / 11.0 / 10.0 / 7.5 m3/min); - Heating (14.0 / 12.5 / 11.0 / 8.5 m3/min). Pipe connections: 1 pc x 6.35 mm (1/4") / 1 pc x 12.7 mm (1/2"). Weight - max 24.0 kg. Infrared remote control and fixing elements in the set. Refrigerant - Freon R32. Integrated condensate pump
16 | Ultra slim duct type indoor unit, designed for multi-split air conditioning systems. Max dimensions 200 x 950 x 500 mm. Un=230 V AC, 50 Hz. Nominal cooling power min 6.0 kW. Nominal heating power min 6.8 kW. It has 4 fan speed levels and includes air filter. Sound pressure level: - Cooling (44 / 38 / 35 / 30 dB (A)); - Heating (45 / 41 / 38 / 33 dB (A)). Total sound power: Cooling - max 60 dB(A); Heating - max 63 dB(A). Air flow: - Cooling (14.5 / 11.5 / 10.5 / 8.0 m3/min); - Heating (15.0 / 13.0 / 11.5 / 9.0 m3/min). Pipe connections: 1 pc x 6.35 mm (1/4") / 1 pc x 12.7 mm (1/2"). Weight - max 24.0 kg. Infrared remote control and fixing elements in the set. Refrigerant - Freon R32. Integrated condensate pump

## REI
No. | Type of equipment requested by BoQ and its data | Bidder’s response
|  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  | Yes, we comply | No, we do not comply (indicate discrepancies)
ItB-26/03305: “Construction of the Administrative building for the provision of social services, with a height regime of S+G+3F, on land with cadastral number 1701115.673, Cahul municipality, loan Voda cel Cumplit street”
1 | Plastic distribution board with solid door and 1 terminal block, applicable, with a capacity of min. 13 modules, IP40, min. dimensions 336 x 300 x 151 mm, equipped with padlock and DIN, N and PE type bars
2 | Plastic distribution board with solid door and 1 terminal block, applicable, with a capacity of min. 18 modules, IP40, IK09, min. dimensions 426 x 300 x 145 mm, equipped with padlock and DIN, N and PE type bars
3 | Central controller for security lighting 5M, according to IEC/EN 62034, compatible with up to 128 luminaires, addressable, Bluetooth configuration and integrated web interface, Bluetooth communication network (2400000...2483500 kHz) 1 mW at 300 m, Ethernet Modbus TCP master, serial links with physical interface 2 x RS232 + 1 x Ethernet, 2 output relays 17-19 V DC, 2 input contacts 3 V DC, 0.2 mA, 1 battery 1 x 3 V LiMnO2, mounting on 35 mm DIN rail, 20 VA, 230 V AC, 50...60 Hz
4 | Addressable line controller module 5M with DALI, RS232, Ethernet, RS485 communication protocol ports, output voltage 18 V 5...235 mA for connecting the control line to the luminaires, with 5 local signaling LEDs, mounting on 35 mm DIN rail, 0.1 A, 220...240 V approx. 50...60 Hz
5 | Plastic distribution board with solid door and 1 terminal block, applicable, with a capacity of min. 36 modules, IP40, IK09, min. dimensions 426 x 450 x 151 mm, equipped with padlock and DIN rails
6 | Plastic distribution board with solid door and 1 terminal block, applicable, with a capacity of min. 48 modules, IP40, IK09, min. dimensions 550 x 450 x 168 mm, equipped with padlock and DIN rails
7 | Luminaire for general indoor lighting, with suspended mounting, equipped with 32W LED, luminous flux 4790 lm, color temperature 4000K, supply voltage 220...240V, CRI>=90, luminous efficiency 149.7 lm/W, lifespan >100000h, min. size 1200x65x65 mm
8 | Lighting fixture for general indoor lighting, with surface mounting on the ceiling, equipped with 15W LED, luminous flux 2160 lm, color temperature 3000K, supply voltage 220-240V, protection degree IP20, impact resistance IK02, CRI>=90, lifespan >100000h, min size 600x110x65 mm
9 | Luminaire for general indoor lighting, with recessed ceiling mounting, equipped with 10W LED, luminous flux 700 lm, color temperature 2700K, supply voltage 220-240V, CRI>=90, luminous efficiency 58 lm/W, protection degree IP20, lifespan >100000h, dimensions Dmin =80 x 110(h) mm
10 | Lighting fixture for general indoor lighting, with surface mounting on ceiling or wall equipped with 24W LED, luminous flux 2620Lm, color temperature 4000K, supply voltage 220-240V, protection degree IP40, impact resistance IK05, luminous efficiency 110lm/W, lifespan >60000h, operating temperature between 0...25 *C, CRI>=80, dimension Dmin =400 x 115 mm
11 | Lighting fixture for general outdoor lighting, with surface mounting on the wall equipped with 17W LED, luminous flux 1800Lm, color temperature 4000K, supply voltage 220-240V, protection degree IP65, impact resistance IK08, presence/motion detection and use of natural light
12 | Security lighting fixture, intended for backup lighting and interventions in risk areas, with surface mounting on the ceiling, equipped with 4.9 W LED, luminous flux of 600 lm, color temperature 4500K, supply voltage 220-240V, protection degree IP65, impact resistance IK02, CRI>=90, autonomy min 3h, integrated LiFePO4 battery, compatible with addressable DALI monitoring and control system, min dimensions 300 x 120 x 60 mm
13 | Security lighting fixture, intended for signaling escape routes, with surface mounting on wall or ceiling, equipped with 3W LED, visibility distance min. 30 m, color temperature 4500K, supply voltage 220...240V, protection degree IP65, impact resistance IK02, autonomy min. 3h, integrated LiFePO4 battery, compatible with addressable DALI monitoring and control system, min. dimensions 350 x 145 x 65 mm
14 | Luminaire for anti-panic security lighting with surface mounting on the ceiling, equipped with 3.5W LED, luminous flux of 190 lm, color temperature 4500K, supply voltage 220-240V, protection degree IP65, impact resistance IK02, CRI>=90, autonomy min 3h, integrated LiFePO4 battery, compatible with addressable DALI monitoring and control system, min dimensions 170 x 170 x 50 mm
15 | Security lighting fixture for escape lighting, with surface mounting on wall or ceiling, equipped with 3.5W LED, luminous flux of 190 lm, color temperature 4500K, supply voltage 220...240V, protection degree IP65, impact resistance IK02, min. 3h autonomy, integrated LiFePO4 battery, compatible with addressable DALI monitoring and control system, min. dimensions 170 x 170 x 50 mm

## RAC
No. | Type of equipment requested by BoQ and its data | Bidder’s response
|  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  | Yes, we comply | No, we do not comply (indicate discrepancies)
ItB-26/03305: “Construction of the Administrative building for the provision of social services, with a height regime of S+G+3F, on land with cadastral number 1701115.673, Cahul municipality, loan Voda cel Cumplit street”
1 | Porcelain washbasin, including for people with disabilities, dimensions LxW - min 70x40 cm, with plastic drain pipe, mounted on the furniture top. Height/Edge thickness: min 130 mm. Material: Sanitary porcelain fired at over 1200°C, treated with an anti-dirt layer (hygienic glaze) that repels limescale and bacteria. Superior configuration: Factory-fitted with 1 central tap hole and overflow hole. Max weight 19 kg
2 | Electric water heater IP24, 220-240 V, with mechanical control, suspended mounted, Plucru = 8 bar, energy efficiency class - C, having hot water storage capacity - min 50 l, dry type heating element power - 1 x 1500 W, maximum water heating temperature - 65 +/- 5*C, max dimensions 640(h)x450x450 mm, with fixing elements and dielectric coupling in the set
3 | Electric water heater IP24, 220-240 V, with mechanical control, suspended mounted, Plucru = 8 bar, energy efficiency class - C, having hot water storage capacity - min 30 l, dry heating element power - 1 x 1500 W, maximum water heating temperature - 65 +/- 5*C, max dimensions 630(h)x340x350 mm, with fixing elements and dielectric coupling in the set
4 | Electric water heater IP24, 220-240 V, with mechanical control, suspended mounted, Plucru = 8 bar, energy efficiency class - C, having hot water storage capacity - min 10 l, dry heating element power - 1 x 1500 W, maximum water heating temperature - 65 +/- 5*C, max dimensions 460(h)x260x265 mm, with fixing elements and dielectric coupling in the set
5 | Wall-hung WC with Slim Soft close system cover on frame for hanging WC Hmax = 82 cm, tested with a max load of 400 kg; corrosion and scratch resistant, with water tank, 2-way flush valve and fixing elements
6 | Basin mixer, with infrared sensor, temperature controller, solenoid valve with 6 V filter (4x 1.5 V AA alkaline batteries), aerator, and 2 flexible connection hoses G 3/8" IG x 380 mm, with integrated non-return valve and pre-filter

## SI
No. | Type of equipment requested by BoQ and its data | Bidder’s response
|  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  | Yes, we comply | No, we do not comply (indicate discrepancies)
ItB-26/03305: “Construction of the Administrative building for the provision of social services, with a height regime of S+G+3F, on land with cadastral number 1701115.673, Cahul municipality, loan Voda cel Cumplit street”
1 | Additional metal box with front door made of electrostatically painted steel, equipped with internal CAN DRIVE communication bus for connecting and extending internal functional modules, front door providing two dedicated cutouts for integrating two control modules with user interface, interior compartmentalized with fixing shelves for storing 2 12V spare batteries, IP31, min external dimensions 433 x 563 x 187 mm, set with fixing elements and mounting accessories
2 | Modular addressable control panel for fire detection and extinguishing systems with architecture based on distributed microprocessors with redundant spare CPU, internal modules interconnected via CAN DRIVE data bus with support for quick replacement in "Hot-Swap" mode, user interface on the front door consisting of a 7-inch color graphic touch screen, advanced signal management with interactive graphic maps and support for IP video verification directly on the screen, expandable hardware structure from 1 to 4 interconnected metal cabinets, detection loop expansion capacity from 2 to 16 addressable loops per control panel, integrated connectivity in Hornet+ type network (up to 48 nodes) or TCP/IP (up to 20 clusters), fully certified according to EN 54-2, EN 54-4, EN 54-21 and EN 12094-1 standards, nominal supply voltage 230 V AC with internal sources of 4 A / 5.2 A and integrated battery charger for backup batteries up to 24 Ah
3 | Addressable optical-acoustic siren, with control capacity for early warning through intermittent light signals and loud sound warnings, provided with direct connection on the addressable loop and integrated short-circuit isolator on the line, the hardware interface being equipped with an internal trimmer for volume calibration and selection from a number of 32 distinct evacuation tones, fully certified with high protection degree IP67 according to European standards EN 54-3, EN 54-17 and EN 54-18, nominal supply and operating voltage Un=19 - 30 VDC, maximum acoustic power generated up to 106 dBA at a distance of max 1 m
4 | Switching power supply with back-up in a metal casing with control capacity for intelligent management of power supply and charging of reserve batteries, provided with direct connection for external load and separate circuit dedicated to battery charging, hardware interface equipped with 3 indicator LEDs for signaling the status of the AC network, batteries and general faults, as well as 2 open collector (OC) fault outputs, fully certified according to European standards EN 50131-6, nominal input voltage of 230 VAC and stabilized output operating voltage Un=13.8 VDC, maximum programmable current supported at the output of 6.2 A distributed as 5 A for external consumers and 1.2 A for battery charging, metal casing having external dimensions of min. 497 x 380 x 87 mm and internal space optimized for hosting 2 12 V batteries with a capacity of up to 17 Ah each Trimiteți feedback
5 | Compact electric smoke control unit, with control capacity for operating electric actuators at 24 VDC, provided with direct connection through potential-free contact inputs (normally closed) for receiving signals from smoke detectors, panic buttons or BMS systems, the hardware interface is equipped with LED indicators for signaling alarm states and network failures, fully certified according to European standards EN 12101-10, nominal supply voltage 100 - 250 VAC and operating voltage on output of 24 VDC, maximum programmable current supported on the power outputs of up to 13 A, integrating internal space for 2 12 VDC backup batteries, external dimensions of min. 400 x 400 x 150 mm
6 | Communication unit with control capacity for high security monitoring and quick dialing via 2 configurable DSS keys in SIP intercom systems, provided with direct connection via two RJ45 ports (Network with PoE 802.3af enabled and LAN for bridging), the hardware interface being equipped with Broadcom main chipset, 2.5 W audio amplifier, external connector for active speaker, analog audio output available for DVR recording and integrated HD video camera, fully certified with IP65 weather protection class and IK10 vandal resistance, compatible with Asterisk, Broadsoft and Elastix platforms, ensuring advanced sound management through narrow and wideband codecs, full-duplex AEC echo cancellation and 5 meter microphone coverage distance, offering support for static IP configuration, DHCP, PPPoE, VPN security, VLAN and dual power options at 12V DC or via PoE class 0, in a robust housing made of cast aluminum alloy resistant to working temperatures of -40...+70 degrees Celsius, min. housing dimensions 220 x 140 x 60 mm

## SPA
No. | Type of equipment requested by BoQ and its data | Bidder’s response
|  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  | Yes, we comply | No, we do not comply (indicate discrepancies)
ItB-26/03305: “Construction of the Administrative building for the provision of social services, with a height regime of S+G+3F, on land with cadastral number 1701115.673, Cahul municipality, loan Voda cel Cumplit street”
1 | Metal cabinet with front door made of electrostatically painted steel, IP31, external dimensions max. 500 x 400 x 150 mm, equipped with padlock, DIN, N and PE bars
2 | Hybrid electronic central module (mainboard of the control panel), for control and signaling, provided on the board with 8 detection zones and expandable up to 32 wired or wireless zones, through dedicated buses for keypads and extension modules, hardware structure offering from 8 to 32 programmable outputs, configuration allowing organization into 16 partitions and 4 independent objects with automatic management through 28 independent timers, equipped with integrated telephone communicator for monitoring, voice messaging and remote control, interface supporting operation through touchscreen or LCD keypads, proximity cards and remote controls, the system accepting 64+4+1 users and storing a log of at least 439 events with printing function, equipped with RS-232 serial port RJ type for firmware update via PC and integrated 1.2 A switching power supply with diagnostics and battery charging, full compliance with the European safety standard EN 50131 Grade 3
3 | Radio and GSM transmitter for transmitting alarm messages and event statuses to a dispatch station, provided with direct connection through 8 normally closed (NC) hardware inputs and serial interface for direct connection of alarm panels, equipped with a detachable antenna with SMA connector and indicator LEDs for signaling the status of the cellular network and data flow, nominal supply and operating voltage Un=12 VDC, with dual operating capacity in 2 digital transmission modes such as SMS or TCP/IP via GPRS and automatic operation on 4 GSM frequency bands 850 / 900 / 1800 / 1900 MHz
4 | Switching mode backup power supply, for powering 12 V DC devices in the security system structure, equipped with a connector for direct integration with modules, hardware structure ensuring a total output current of 4 A and allowing operation with or without a sealed lead-acid backup battery, configuration including advanced circuits for battery status monitoring, complete short circuit, overload and deep discharge protection, DIP switches for selecting the charging current of 0.5 A or 1 A, the interface being equipped with LED optical indicators for network, battery and overload, 3 OC (open collector) outputs for remote signaling of failures and local audible alarm, constructive design allowing easy mounting on a 35 mm DIN rail or in dedicated housings, fully certified according to the European safety standard EN 50131-6 Grade 2
5 | Hybrid central keypad with LCD screen and protective cover, designed for daily operation and programming of burglar alarm systems, with backlit keys and display, equipped with an integrated card and proximity tag reader (EM 125 kHz standard), hardware structure including 2 programmable detection zones on the board with full support for EOL, 2EOL and 3EOL configurations, LCD alphanumeric display screen with a standard configuration of 2 lines x 16 characters, LED optical indicators for system status, dedicated keys for quick triggering of Panic, Fire and Help/Medical alarms, integrated acoustic signaling for selected events and an RS-232 RJ type serial port for direct interfacing with the GUARDX management software, maximum current consumption being 110 mA at a nominal voltage of 12 V DC, ensuring full compliance with the European standard EN 50131 Grade 3
6 | Combined PIR motion and glass break detector, integrating a passive infrared sensor (PIR) and Quad Linear Imaging technology, for accurate analysis of human body dimensions, along with a digital acoustic detector for breaking and cutting glass based on frequency spectrum and shock wave analysis, the hardware structure offers a detection range of up to 15 m for the IR channel (90 degree angle) and up to 10 m for the acoustic channel, the configuration ensuring adjustable immunity to pets weighing between 15 and 25 kg, equipped with bidirectional temperature compensation, separate sensitivity calibration for both channels through dedicated potentiometers, 2 independent relay outputs with NC type contacts (28 V DC, 0.1 A) and tamper protection microcontact, optical indicators with 3 dedicated LEDs, the power supply being made at a nominal voltage between 8.2 V and 16 V DC with a low current consumption of 18 mA in standby mode and 25.5 mA in alarm mode
7 | Hybrid opto-acoustic warning device (wired siren), impact-resistant ABS body, IP 31, for local signaling of alarm states via an internal piezoelectric speaker with a strong acoustic pressure of 110 dB at a distance of 1 meter, and an integrated strobe (flash) lamp with a warning frequency of approximately 150 flashes per minute, configurable for independent control of the two components for operation in 3 distinct modes, supply voltage 10 - 14 V DC with an optimized current consumption of 200 mA for the audio channel and 250 mA for the optical indicator

## TS
No. | Type of equipment requested by BoQ and its data | Bidder’s response
|  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  | Yes, we comply | No, we do not comply (indicate discrepancies)
ItB-26/03305: “Construction of the Administrative building for the provision of social services, with a height regime of S+G+3F, on land with cadastral number 1701115.673, Cahul municipality, loan Voda cel Cumplit street”
1 | RACK 19" 42U floor-standing telecommunications and networking cabinet, 600x800 mm, black color, disassembled (in set including legs, wheels), with perforated front / rear doors; with min. 6 x Blank panels, with tool-less mounting, with 2 vertical cable management, equipped with 4 fan block on top with environmental monitoring (temperature and humidity detectors)
2 | Telecommunications and networking wall cabinet 15U, 600x600 mm, 19" black, disassembled, with fans, with perforated front/rear doors; with tool-less mounting, with 2 vertical cable management
3 | Router / firewall security equipment with: min. 8 RJ-45 10/100/1000Base-T ports + min. 2 SFP+ 1/10 Gbps ports; Firewall throughput min. 2 Gbps; VPN throughput min. 500 Mbps; Low latency for real-time traffic; Support: NAT, PAT, Static routing IPv4 / IPv6, Policy-based routing; Security functions: stateful firewall, IDS / IPS or equivalent, traffic filtering, application control; VPN: IPSec, SSL VPN; Authentication: RADIUS, LDAP or equivalent; Monitoring: SNMP, Syslog. Management: Web (HTTPS), CLI, SSH; 19", 1U format; Power supply 230V AC; Power consumption: max. 150W
4 | Aggregation switch with: min. 24 RJ-45 10/100/1000Base-T ports + uplink module with min. 8 SFP+ ports 1/10 Gbps + min. 4 SFP+ transceivers 10 Gbps, 1310 nm, up to 10 km. Throughput min. 130 Mpps; Switching capacity min. 480 Gbps; Network Latency < 3.5 ms (1000 Mb, 64 byte packet size); Packet buffer min. 6MB; Static (IPv4 / IPv6): min. 4000 IPv4 / 2000 IPv6; VLAN 802.1Q (up to 4094 VLANs), QoS 802.1p, LLDP / LLDP-MED, LACP (802.3ad), Flow Control, STP / RSTP / MSTP, IGMP Snooping v1 / v2 / v3, MLD Snooping v1 / v2, IGMP Querier, IPv4 / IPv6 static routing, ARP / NDP, ICMP / ICMPv6; Security: RADIUS, TACACS+, 802.1X, DHCP Snooping, Dynamic ARP Inspection, IP Source Guard, Port Security, IPv4 / IPv6 / MAC access lists (ACL); Monitoring: sFlow or equivalent, SNMP v1 / v2c / v3, Syslog, RMON; Administration: CLI, Web (HTTP / HTTPS), SSH; Support for stacking or equivalent; 19" format, 1U. Power supply: 2 redundant power supplies (1+1), hot-swappable, 230V AC power supply; Power consumption: max. 350W
5 | Access switch type 1, with min. 24 RJ-45 10/100/1000Base-T ports; Uplink: min. 4 SFP+ 1/10 Gbps ports; Throughput min. 95 Mpps; Switching capacity min. 128 Gbps; Network Latency < 4 ms (1000 Mb, 64 byte packet size); Packet buffer min. 3MB; VLAN 802.1Q (min. 512 VLANs), QoS 802.1p, LLDP/LLDP-MED, LACP (802.3ad), Flow Control, STP / RSTP / MSTP, IGMP Snooping v1 / v2 / v3; Security: 802.1X, Port Security, DHCP Snooping, Dynamic ARP Inspection, IP Source Guard, ACL IPv4 / IPv6 / MAC; Monitoring: SNMP v1/v2c/v3, Syslog; Administration: CLI, Web (HTTP / HTTPS), SSH; 19" format, 1U. Power supply 230V AC. Power consumption: max. 125W
6 | Access switch type 2 with min. 48 RJ-45 10/100/1000Base-T ports; Uplink: min. 4 SFP+ 1/10 Gbps ports; Throughput min. 140 Mpps; Switching capacity min. 128 Gbps; Network Latency < 4 ms (1000 Mb, 64 byte packet size); Packet buffer min. 3MB; VLAN 802.1Q (min. 512 VLANs), QoS 802.1p, LLDP / LLDP-MED, LACP (802.3ad), Flow Control, STP / RSTP / MSTP, IGMP Snooping v1 / v2 / v3; Security: 802.1X, Port Security, DHCP Snooping, Dynamic ARP Inspection, IP Source Guard, ACL IPv4 / IPv6/MAC; Monitoring: SNMP v1 / v2c / v3, Syslog; Administration: CLI, Web (HTTP / HTTPS), SSH; 19" format, 1U. Power supply 230V AC. Power consumption: max. 125W
7 | Access switch type 3 with: min. 24 RJ-45 10/100/1000Base-T PoE+ ports; Uplink: min. 4 SFP+ 1/10 Gbps ports; Throughput min. 95 Mpps; Switching capacity min. 128 Gbps; Network Latency < 4 ms (1000 Mb, 64 byte packet size); Packet buffer min. 3MB; VLAN 802.1Q, QoS 802.1p, LLDP /LLDP-MED, LACP, Flow Control, STP / RSTP / MSTP, IGMP Snooping; Security: 802.1X, DHCP Snooping, DAI, IP Source Guard; Monitoring: SNMP v1 / v2c / v3, Syslog; Administration: CLI, Web, SSH; PoE standard: IEEE 802.3af/at; PoE budget: min. 370 W; 19" format, 1U; Power supply 230V AC. Power consumption: max. 600W
8 | Indoor Wi-Fi access point, ceiling or wall mounting; network interface: min. 1xRJ-45 1 Gbps with PoE power supply (IEEE 802.3af/at); frequency support: 2.4 GHz and 5 GHz; supported standards: IEEE 802.11 a/b/g/n/ac/ax (Wi-Fi 4/5/6); aggregate wireless speed: min. 2.5-3.0 Gbps; channel width: 20/40/80 MHz; integrated omni-directional antennas; functions: MU-MIMO, OFDMA, BSS Coloring, band steering, WPA2/WPA3; support for multiple SSIDs (min. 8), VLAN support per SSID; centralized management via controller
9 | Relay control unit and transmission of dry contact status via local Ethernet network, supply voltage - 12 V, IP40, max dimensions 162 x 103 x 35 mm, humidity during operation - up to 80%
10 | Controller for managing 2 doors, 4 readers and 2 locks, including power supply, batteries, RJ45, 24V, in metal enclosure
11 | Controller for managing 4 doors, 8 readers and 4 locks, including power supply, batteries, RJ45, 24V, in metal enclosure
12 | Mifare reader with the following features: - 12V DC power supply, power consumption - 2 W; - overall dimensions (LxHxB) - max 44x115x22 mm; - reading distance - <=50 mm; - working frequency - 13.56 MHz; - connection interface - RS-485 / Wiegand; - power and status indicator; - protection degree - IP65, IK10.
13 | Electromechanical lock with built-in mounting screw with the following characteristics: - holding force min 1000 kg; - power supply 12V DC, 900 (working) / 120 (stand by) mA; - overall dimensions (LxHxB) - max 27x192x25 mm; - status indicator; - protection degree - IP65, IK10.
14 | Contactless Mifare smart card, card reading frequency min. 13.56 MHz, with the possibility of printing on the card surface, max. dimensions 85.5 mm x 54 mm x 0.8 mm

## Fotovoltaic
No. | Type of equipment requested by BoQ and its data | Bidder’s response
|  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  | Yes, we comply | No, we do not comply (indicate discrepancies)
ItB-26/03305: “Construction of the Administrative building for the provision of social services, with a height regime of S+G+3F, on land with cadastral number 1701115.673, Cahul municipality, loan Voda cel Cumplit street”
1 | Plastic distribution board with solid door and 1 terminal block, applicable, with a capacity of 18 modules, IP40, IK09, dimensions 426 x 300 x 145 mm, equipped with padlock and DIN, N and PE type bars
2 | Monocrystalline Half-Cell photovoltaic panel, 72 cells (144 half-cells). Nominal power (Pmax): 585 W. Module efficiency: min 22.4%. Maximum power voltage (Vmp): 44.21 V. Maximum power current (Imp): 13.24 A. Open circuit voltage (Voc): 52.36 V. Short circuit current (Isc): 14.27 A. Maximum system voltage: 1500 V DC. Cell technology: Monocrystalline Half-Cell (144 half-cells). Classic structure: Glass / EVA / Cells / EVA / Backsheet. Frame: Anodized aluminum (corrosion resistant). Connectors: MC4 (the industry standard for secure connections). Protection degree: IP68 (completely dust and water tight junction box). Max dimensions: 2281 x 1134 x 30 mm. Max weight: 27.2 kg. Max load (Snow): 5400 Pa. Max load (Wind): 2400 Pa.
3 | Three-phase inverter with LED indicator, efficiency up to 98.50%, maximum power of connected photovoltaic panels PmaxDC=27.5kW (DC input), generated power PmaxAC=25.0 kW (AC output), 3 independent MPPT inputs, continuous grounding monitoring (integrated), continuous network status monitoring (integrated), DC reverse polarity protection (integrated), DC/AC overvoltage protection (integrated/integrated), maximum input voltage 1 100 V, nominal voltage 160...1000 V, MPPT input current = 3x30.0 A, nominal output voltage 400V/50Hz, output current 3x40.0A, IP65