| Major repairs and modernisation of the tpieceing block at M. Eminescu High School, Cantemir | Form No. 2 WinСmeta |
| --- | --- |
| (name of the project) |  |

LOCAL QUOTATION No. 2-1-4, Part 2

Ventilation system

| No. No. | Symbol, standards and resource code | Works and expenses | Unit | Quantity as per project data | Estimated value, lei |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Per unit of measure ———— incl. wages | Total ————— incl. salary |

| 1 |  | 2 |  | 3 |  |  | 4 |  | 5 |  |  | 6 |  | 7 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 1. Value of the machinery |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 1.1. AR-1 |  |  |  |  |  |  |  |  |  |  |
| 1 |  | Market price |  | Supply and extract ventilation system with heat recovery, with supply air flow rate: L=7,150 m²/h, P=600 Pa. Fan N=5.2 kW; n=2,130 rpm; I=8.4 A; U=400 V on the intake side: L=5,690 m²/h, P=600 Pa; fan N=5.2 kW; n=2,130 rpm; I=8.4 A; U=400 V, in addition: electric pre-heater Q=19.0 kW/h from -16 °C to -8 °C, counter-flow plastic plate heat exchanger with a minimum energy efficiency of 60%, Q=40.23 kW/h from -8.0 to +8.8 °C; filter with filtration class M5 on the discharge side, filter with filtration class G4 on the intake side, water coil for air heating with anti-freeze system and mixing unit included, Q = 26.82 kW/h from +8.8 to +20*C, C, automation system to be included with the unit, model Duplex 10000 Multi, |  |  | 1 set |  | 1.000 |  |  |  |  |  |
| 2 |  | Market price |  | LDR-900-400-1200 noise attenuator |  |  | piece |  | 1.000 |  |  |  |  |  |
| 3 |  | Market price |  | LDR -1150-400-1200 noise attenuator |  |  | piece |  | 1.000 |  |  |  |  |  |
| 4 |  | Market price |  | Rectangular fire damper for ducts, suitable for wall-mounted installation, with EI60 fire resistance rating, Helmer -60-NO- 400x200 K-MB24-0 |  |  | piece |  | 1.000 |  |  |  |  |  |
| 5 |  | Market price |  | Rectangular fire damper for ducts, suitable for wall-mounted installation, with EI60 fire resistance rating, Helmer -60-NO- 600x250 K-MB24-0 |  |  | piece |  | 3.000 |  |  |  |  |  |
| 6 |  | Market price |  | Rectangular fire damper for ducts, suitable for wall-mounted installation, with EI60 fire resistance rating, Helmer -60-NO- 650x250 K-MB24-0 |  |  | piece |  | 1.000 |  |  |  |  |  |
| 7 |  | Market price |  | Rectangular fire damper for ducts, suitable for wall-mounted installation, with EI60 fire resistance rating, Helmer -60-NO- 700x250 K-MB24-0 |  |  | piece |  | 1.000 |  |  |  |  |  |
| 8 |  | Market price |  | Manual flow regulator for hydraulic adjustment of the KP 100 system |  |  | piece |  | 16.000 |  |  |  |  |  |
| 9 |  | Market price |  | Manual flow regulator for the KP 150 hydraulic control system ( ) |  |  | piece |  | 11.000 |  |  |  |  |  |
| 10 |  | Market price |  | Manual flow regulator for hydraulic adjustment of the KP 160 system |  |  | piece |  | 24.000 |  |  |  |  |  |
| 11 |  | Market price |  | Manual flow regulator for hydraulic adjustment of the KP 180 system |  |  | piece |  | 4.000 |  |  |  |  |  |
| 12 |  | Market price |  | Manual flow regulator for hydraulic adjustment of the KP 200 system |  |  | piece |  | 1.000 |  |  |  |  |  |
| 13 |  | Market price |  | Manual flow regulator for hydraulic adjustment of the KP 225 system |  |  | piece |  | 6.000 |  |  |  |  |  |
|  |  |  |  | Total AR-1 Including salary |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 1.2. AR-2 |  |  |  |  |  |  |  |  |  |  |
| 14 |  | Market price |  | Supply and extract ventilation system with heat recovery, with supply air flow rate: L=7030 m²/h, P=600 Pa. Fan N=5.2 kW; n=2570 rpm; I=8.4 A; U=400 V on the intake side: L=6,170 m²/h, P=600 Pa; fan N=5.2 kW; n=2,570 rpm; I=8.4 A; U=400 V, additionally: electric pre-heater Q=19.0 kW/h from -16 °C to -7.9 °C, counter-flow plastic plate heat exchanger with a minimum energy efficiency of 60%, Q=39.42 kW/h from -7.9 °C to +8.84 °C* filter, with filtration class M5 on the discharge side, filtration class G4 filter on the intake side, water coil for air heating with anti-freeze system and mixing unit included, Q = 26.82 kW/h from +8.84 to +20*C, C, automation system to be included with the unit, model Duplex 10000 Multi, |  |  | 1 set |  | 1.000 |  |  |  |  |  |
| 15 |  | Market price |  | LDR-1000-400-1200 noise attenuator |  |  | piece |  | 1.000 |  |  |  |  |  |
| 16 |  | Market price |  | LDR -1050- 400-1200 noise attenuator |  |  | piece |  | 1.000 |  |  |  |  |  |
| 17 |  | Market price |  | Rectangular fire damper for ducts, suitable for wall-mounted installation, with EI60 fire resistance rating, Helmer -60-NO- 500x250 K-MB24-0 |  |  | piece |  | 1.000 |  |  |  |  |  |
| 18 |  | Market price |  | Rectangular fire damper for ducts, suitable for wall-mounted installation, with EI60 fire resistance rating, Helmer -60-NO- 600x250 K-MB24-0 |  |  | piece |  | 2.000 |  |  |  |  |  |
| 19 |  | Market price |  | Rectangular fire damper for ducts, suitable for wall-mounted installation, with EI60 fire resistance rating, Helmer -60-NO- 650x250 K-MB24-0 |  |  | piece |  | 3.000 |  |  |  |  |  |
| 20 |  | Market price |  | Manual flow regulator for hydraulic adjustment of the KP 100 system |  |  | piece |  | 2.000 |  |  |  |  |  |
| 21 |  | Market price |  | Manual flow regulator for hydraulic adjustment of the KP 140 system |  |  | piece |  | 2.000 |  |  |  |  |  |
| 22 |  | Market price |  | Manual flow regulator for hydraulic adjustment of the KP 150 system |  |  | piece |  | 20.000 |  |  |  |  |  |
| 23 |  | Market price |  | Manual flow regulator for hydraulic adjustment of the KP 160 system |  |  | piece |  | 14.000 |  |  |  |  |  |
| 24 |  | Market price |  | Manual flow regulator for hydraulic adjustment of the KP 180 system |  |  | piece |  | 4.000 |  |  |  |  |  |
| 25 |  | Market price |  | Manual flow regulator for hydraulic adjustment of the KP 200 system |  |  | piece |  | 2.000 |  |  |  |  |  |
| 26 |  | Market price |  | Manual flow regulator for hydraulic adjustment of the KP 225 system |  |  | piece |  | 9.000 |  |  |  |  |  |
| 27 |  | Market price |  | Manual flow regulator for hydraulic adjustment of the KP 250 system |  |  | piece |  | 1.000 |  |  |  |  |  |
|  |  |  |  | Total AR-2 Including salary |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 1.3. AR-11 |  |  |  |  |  |  |  |  |  |  |
| 28 |  | Market price |  | Supply and extract ventilation system with heat recovery, with supply air flow rate: L=1150 m²/h, P=350 Pa. Fan N=0.78 kW; n=2970 rpm; I=3.9 A; U=230 V on the intake side: L=1150 m²/h, P=350 Pa; fan N=0.78 kW; n=2970 rpm; I=3.9 A; U=230 V, additionally: counter-flow plastic-plate heat exchanger with a minimum energy efficiency of 60 per cent, Q=8.2 kW/h from –16 to –5.3 °C, filter, with filtration class M5 on the supply side, filter with filtration class G4 on the intake side, water coil for air heating, Q = 7.9 kW/h from –5.6 to +18 °C, C, automation system to be supplied with the unit, model Duplex 1500 Multi-V |  |  | 1 set |  | 1.000 |  |  |  |  |  |
| 29 |  | Market price |  | LDС-315-900 noise attenuator |  |  | piece |  | 2.000 |  |  |  |  |  |
|  |  |  |  | Total AR-11 Including wages |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 1.4. AR-12 |  |  |  |  |  |  |  |  |  |  |
| 30 |  | Market price |  | Supply and extract ventilation system with heat recovery, with supply air flow rate: L=2620 m²/h, P=350 Pa. Fan N=2.2 kW; n=2970 rpm; I=3.8 A; U=400 V on the intake side: L=2,845 m²/h, P=350 Pa; fan N=2.2 kW; n=2,970 rpm; I=3.8 A; U=400 V, additionally: counter-flow plastic plate heat exchanger with a minimum energy efficiency of 60 per cent, Q=17.90 kW/h from –16 to +4.4 °C, filter, with filtration class M5 on the supply side, filter with filtration class G4 on the return side, water coil for air heating, Q = 11.39 kW/h from +4.4 to +18 °C, C, automation system to be supplied with the unit, model Duplex 3500 Multi-V |  |  | 1 set |  | 1.000 |  |  |  |  |  |
| 31 |  | Market price |  | LDR-500-400-1200 noise attenuator |  |  | piece |  | 1.000 |  |  |  |  |  |
| 32 |  | Market price |  | LDR -600-400-1200 noise attenuator |  |  | piece |  | 1.000 |  |  |  |  |  |
| 33 |  | Market price |  | Manual flow regulator for hydraulic adjustment of the KP 150 system |  |  | piece |  | 2.000 |  |  |  |  |  |
| 34 |  | Market price |  | Manual flow regulator for hydraulic adjustment of the KP 225 system |  |  | piece |  | 9.000 |  |  |  |  |  |
| 35 |  | Market price |  | Manual flow regulator for hydraulic adjustment of the KP 250 system |  |  | piece |  | 2.000 |  |  |  |  |  |
|  |  |  |  | Total AR-12 Including salary |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 1.5. A-13 |  |  |  |  |  |  |  |  |  |  |
| 36 |  | Market price |  | Extraction ventilation system L=300 m³/h, P=200 Pa – Axial fan VKM-160 N=0.098 kW, n=2705 rpm, l=0.43 A, U=230 V |  |  | 1 set |  | 1.000 |  |  |  |  |  |
| 37 |  | Market price |  | KOM 160 non-return valve |  |  | piece |  | 1.000 |  |  |  |  |  |
| 38 |  | Market price |  | VVGF 160 elastic mount |  |  | piece |  | 2.000 |  |  |  |  |  |
| 39 |  | Sistemair |  | SR 160/900 noise attenuator |  |  | piece |  | 1.000 |  |  |  |  |  |
| 40 |  | Market price |  | Manual flow regulator for hydraulic adjustment of the KP 100 system |  |  | piece |  | 4.000 |  |  |  |  |  |
| 41 |  | Market price |  | Manual flow regulator for hydraulic adjustment of the KP 125 system |  |  | piece |  | 1.000 |  |  |  |  |  |
|  |  |  |  | Total A-13 Including salary |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 1.6. A-14 |  |  |  |  |  |  |  |  |  |  |
| 42 |  | Market price |  | Extraction ventilation system L=460 m³/h, P=200 Pa – Axial fan VKMS-160 N=0.116 kW, n=2625 rpm, l=0.52 A, U=230 V |  |  | 1 set |  | 1.000 |  |  |  |  |  |
| 43 |  | Market price |  | KOM 160 non-return valve |  |  | piece |  | 1.000 |  |  |  |  |  |
| 44 |  | Market price |  | VVGF 160 elastic mount |  |  | piece |  | 2.000 |  |  |  |  |  |
| 45 |  | Sistemair |  | SR 160/900 noise attenuator |  |  | piece |  | 1.000 |  |  |  |  |  |
| 46 |  | Market price |  | Manual flow regulator for hydraulic adjustment of the KP 160 system |  |  | piece |  | 2.000 |  |  |  |  |  |
|  |  |  |  | Total A-14 Including wages |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 1.7. A-15 |  |  |  |  |  |  |  |  |  |  |
| 47 |  | Market price |  | Extraction ventilation system L=900 m³/h, P=350 Pa – axial fan VKMS-315 N=0.296 kW, n=2720 rpm, l=1.34 A, U=230 V |  |  | 1 set |  | 1.000 |  |  |  |  |  |
| 48 |  | Market price |  | KOM 315 non-return valve |  |  | piece |  | 1.000 |  |  |  |  |  |
| 49 |  | Market price |  | VVGF 315 elastic mount |  |  | piece |  | 2.000 |  |  |  |  |  |
| 50 |  | Sistemair |  | SR 315/900 noise attenuator |  |  | piece |  | 1.000 |  |  |  |  |  |
| 51 |  | Market price |  | Manual flow regulator for hydraulic adjustment of the KP 140 system |  |  | piece |  | 6.000 |  |  |  |  |  |
|  |  |  |  | Total A-15 Including salary |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 1.8. Smoke extraction ventilation system |  |  |  |  |  |  |  |  |  |  |
| 52 |  | Market price |  | Smoke extraction system L=21,000 m³/h, P=500 Pa – OCA 501-063-N-00550/2 axial fan, A100L2 electric motor, N=5.5 kW, n=2,870 rpm, u=380 V |  |  | piece |  | 1.000 |  |  |  |  |  |
| 53 |  | Market price |  | Elastic mount СОМ-ОСА-063 |  |  | piece |  | 2.000 |  |  |  |  |  |
| 54 |  | Market price |  | Shut-off valve REG-L-630-N-LMV-D3LON |  |  | piece |  | 1.000 |  |  |  |  |  |
| 55 |  | Market price |  | Fire damper, wall-mounted, normally closed/with 24V actuator – KPU-1N-NZ-1700x1000-1kf=MP24 |  |  | piece |  | 3.000 |  |  |  |  |  |
|  |  |  |  | Total Smoke extraction ventilation system Including wages |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | Direct costs |  |  | lei |  |  |  |  |  |  |  |
|  |  |  |  | Storage costs |  |  | % |  |  |  |  |  |  |  |
|  |  |  |  | Total value of machinery Including wages |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 2. Installation work |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 2.1. AR-1 |  |  |  |  |  |  |  |  |  |  |
| 56 |  | VC18A |  | Installation of the special, modulated air-handling unit (Supply and return ventilation system with heat recovery, with supply air flow rate: L=8,920 m²/h, P=600 Pa – Duplex 11000 Multi model) |  |  | piece |  | 1.000 |  |  |  |  |  |
| 57 |  | VC29A |  | Installation of the air heater, with filter bags, with a total weight of 50–200 kg (included in the set) |  |  | piece |  | 1.000 |  |  |  |  |  |
| 58 |  | VC08A |  | Installation of a type V air filter, with automatic cleaning, fan and dust collection container, weighing 200–600 kg (included in the set) |  |  | piece |  | 2.000 |  |  |  |  |  |
| 59 |  | VB18A |  | Rectangular noise attenuator with a perimeter of 1,000–2,000 mm (LDR-900-400-1200; LDR-1100-400-1200) |  |  | piece |  | 2.000 |  |  |  |  |  |
| 60 |  | VC10A |  | Air filter assembly, with bags for dust extraction systems, fitted to fan suction ducts (FSA), for filtration, (-Helmer -60-NO- 500x250 K-MB24-0, 550x250) |  |  | piece |  | 2.000 |  |  |  |  |  |
| 61 |  | VC10A |  | Installation of air filter, with bags for dust extraction systems, fitted to fan suction ducts (FSA), for filtration, (Helmer -60-NO- 600x250 K-MB24-0, 700x250) |  |  | piece |  | 2.000 |  |  |  |  |  |
| 62 |  | VC10A |  | Installation of an air filter with bags for dust extraction systems, fitted to the fan’s (FSA) intake ducts for filtration (Helmer -60-NO- 750x250 K-MB24-0) |  |  | piece |  | 1.000 |  |  |  |  |  |
| 63 |  | VC10A |  | Installation of air filter, with bags for dust extraction systems, fitted to fan intake ducts ( ) (FSA), for filtration, (Helmer -60-NO- 800x250 K-MB24-0) |  |  | piece |  | 1.000 |  |  |  |  |  |
| 64 |  | ID05E |  | Flanged gate valve or butterfly valve with check valve, for central heating systems, with a nominal diameter of 150 mm (Manual flow regulator for hydraulic adjustment of the KP 100, КР150, КР160 systems) |  |  | piece |  | 42.000 |  |  |  |  |  |
| 65 |  | ID05F |  | Valve with drawer or valve and check valve, flanged, for central heating systems, with a nominal diameter of 200 mm (Manual flow regulator for hydraulic balancing of the KP 180, КР200 system) |  |  | piece |  | 4.000 |  |  |  |  |  |
| 66 |  | ID05G |  | Gate valve or ball valve with check valve, flanged, for central heating systems, with a nominal diameter of 250 mm (Manual flow regulator for hydraulic balancing of the KP225 and KP250 systems) |  |  | piece |  | 14.000 |  |  |  |  |  |
|  |  |  |  | Total AR-1 Including wages |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 2.2. AR-2 |  |  |  |  |  |  |  |  |  |  |
| 67 |  | VC18A |  | Installation of the special, modulated air-handling unit (supply and return ventilation system with heat recovery, with supply air flow rate: L=7030 m²/h, P=600 Pa – Duplex 10000 Multi model) |  |  | piece |  | 1.000 |  |  |  |  |  |
| 68 |  | VC29A |  | Installation of the air heating coil, with filter bags, with a total weight of 50–200 kg (included in the set) |  |  | piece |  | 1.000 |  |  |  |  |  |
| 69 |  | VC08A |  | Installation of a type V air filter, with automatic cleaning, fan and dust collection container, weighing 200–600 kg (included in the set) |  |  | piece |  | 2.000 |  |  |  |  |  |
| 70 |  | VB18A |  | Rectangular noise attenuator with a perimeter of 1,000–2,000 mm (LDR-1000-400-1200; LDR- 1050-400-1200) |  |  | piece |  | 2.000 |  |  |  |  |  |
| 71 |  | VC10A |  | Air filter assembly, with bags for dust extraction systems, fitted to fan suction ducts (FSA), for filtration, (-Helmer -60-NO- 500x250 K-MB24-0) |  |  | piece |  | 1.000 |  |  |  |  |  |
| 72 |  | VC10A |  | Installation of air filter, with bags for dust extraction systems, fitted to fan suction ducts (FSA), for filtration, (Helmer -60-NO- 600x250 K-MB24-0) |  |  | piece |  | 2.000 |  |  |  |  |  |
| 73 |  | VC10A |  | Installation of an air filter with bags for dust extraction systems, fitted to the fan’s (FSA) intake ducts for filtration (Helmer -60-NO- 650x250 K-MB24-0) |  |  | piece |  | 3.000 |  |  |  |  |  |
| 74 |  | ID05E |  | Flanged gate valve or butterfly valve with check valve, for central heating systems, with a nominal diameter of 150 mm (Manual flow regulator for hydraulic balancing of the KP 100, КР140, КР150, КР160 systems) |  |  | piece |  | 38.000 |  |  |  |  |  |
| 75 |  | ID05F |  | Valve with drawer or valve and check valve, flanged, for central heating systems, with a nominal diameter of 200 mm (Manual flow regulator for hydraulic balancing of the KP 180, КР200 system) |  |  | piece |  | 6.000 |  |  |  |  |  |
| 76 |  | ID05G |  | Gate valve or ball valve with check valve, flanged, for central heating systems, with a nominal diameter of 250 mm (Manual flow regulator for hydraulic balancing of the KP225 and KP250 systems) |  |  | piece |  | 10.000 |  |  |  |  |  |
| 77 |  | VC18A |  | Installation of a special, modulating air-handling unit (Supply and return ventilation system with heat recovery, with supply air flow rate: L=1,400 m²/h, P=400 Pa – , model Duplex 1500 Multi) |  |  | piece |  | 1.000 |  |  |  |  |  |
| 78 |  | VC29A |  | Installation of the air heating coil, with filter bags, with a total weight of 50–200 kg (included in the set) |  |  | piece |  | 1.000 |  |  |  |  |  |
| 79 |  | VC08A |  | Installation of a type V air filter, with automatic cleaning, fan and dust collection container, weighing 200–600 kg (included in the set) |  |  | piece |  | 2.000 |  |  |  |  |  |
| 80 |  | VB18A |  | Rectangular noise attenuator with a perimeter of 1,000–2,000 mm (LDR-400-300-1200 noise attenuator) |  |  | piece |  | 2.000 |  |  |  |  |  |
| 81 |  | ID05E |  | Flanged valve with drawer or valve and check valve, for central heating systems, with a nominal diameter of 150 mm (Manual flow regulator for hydraulic balancing of the system: КР150, КР160) |  |  | piece |  | 4.000 |  |  |  |  |  |
| 82 |  | ID05G |  | Gate valve or ball valve with check valve, flanged, for central heating systems, with a nominal diameter of 250 mm (Manual flow regulator for hydraulic balancing of the KP225 system) |  |  | piece |  | 2.000 |  |  |  |  |  |
|  |  |  |  | Total AR-2 Including wages |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 2.3. AR-11 |  |  |  |  |  |  |  |  |  |  |
| 83 |  | VC18A |  | Installation of a special, modulated air-handling unit (supply and return ventilation system with heat recovery, supply air flow rate: L = 1150 m²/h, – Duplex 1500 Multi model) |  |  | piece |  | 1.000 |  |  |  |  |  |
| 84 |  | VC29A |  | Installation of the air heating coil, with filter bags, with a total weight of 50–200 kg (included in the set) |  |  | piece |  | 1,000 |  |  |  |  |  |
| 85 |  | VC08A |  | Installation of a type V air filter, with automatic cleaning, fan and dust collection container, weighing 200–600 kg (included in the set) |  |  | piece |  | 2.000 |  |  |  |  |  |
| 86 |  | VB17B |  | AZC-type circular noise attenuator with a circumference of 1,600–2,500 mm (LDС-315-900 noise attenuator) |  |  | piece |  | 2.000 |  |  |  |  |  |
|  |  |  |  | Total AR-11 Including wages |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 2.4. AR-12 |  |  |  |  |  |  |  |  |  |  |
| 87 |  | VC18A |  | Installation of the special, modulated air-handling unit (supply and return ventilation system with heat recovery, with supply air flow rate: L=2620 m²/h, P=450 Pa – Duplex 3500 Multi-V model) |  |  | piece |  | 1.000 |  |  |  |  |  |
| 88 |  | VC29A |  | Installation of the air heating coil, with filter bags, with a total weight of 50–200 kg (included in the set) |  |  | piece |  | 1.000 |  |  |  |  |  |
| 89 |  | VC08A |  | Installation of a type V air filter, with automatic cleaning, fan and dust collection container, weighing 200–600 kg (included in the set) |  |  | piece |  | 2.000 |  |  |  |  |  |
| 90 |  | VB18A |  | Noise attenuator, rectangular with a perimeter of 1000–2000 mm (LDR-500-400-1200 noise attenuator; LDR 600-400-1200) |  |  | piece |  | 2.000 |  |  |  |  |  |
| 91 |  | ID05E |  | Flanged gate valve or ball valve with check valve, for central heating systems, with a nominal diameter of 150 mm (Manual flow regulator for hydraulic balancing of the system КР150) |  |  | piece |  | 2.000 |  |  |  |  |  |
| 92 |  | ID05G |  | Gate valve or valve with check valve, flanged, for central heating systems, with a nominal diameter of 250 mm (Manual flow regulator for hydraulic adjustment of the KP225,250 system) |  |  | piece |  | 11.000 |  |  |  |  |  |
|  |  |  |  | Total AR-12 Including wages |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 2.5. A-13 |  |  |  |  |  |  |  |  |  |  |
| 93 |  | VC01B |  | Installation of centrifugal fans, with a total weight of 50–400 kg, mounted on a metal frame (VKM-160 axial fan) |  |  | piece |  | 1.000 |  |  |  |  |  |
| 94 |  | AcB09A |  | Installation of electric valve actuators, |  |  | piece |  | 1.000 |  |  |  |  |  |
| 95 |  | ID05E |  | Flanged gate valve or globe valve with check valve, for central heating systems, with a nominal diameter of 150 mm (KOM 160 check valve) |  |  | piece |  | 1.000 |  |  |  |  |  |
| 96 |  | VC24A |  | Elastic fan mounting, with rubber elastic mounts (Elastic mount VVGF-160) |  |  | piece |  | 2.000 |  |  |  |  |  |
| 97 |  | VB17A |  | AZC-type circular noise attenuator with a circumference of 800–1,600 mm (SR 160/900) |  |  | piece |  | 1.000 |  |  |  |  |  |
| 98 |  | ID05E |  | Flanged gate valve or ball valve with check valve, for central heating systems, with a nominal diameter of 150 mm (Manual flow regulator for hydraulic balancing of the KP 100, КР125 system) |  |  | piece |  | 5.000 |  |  |  |  |  |
|  |  |  |  | Total A-13 Including wages |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 2.6. A-14 |  |  |  |  |  |  |  |  |  |  |
| 99 |  | VC01B |  | Installation of centrifugal fans, with a total weight of 50–400 kg, mounted on a metal frame (VKMS-160 axial fan) |  |  | piece |  | 1.000 |  |  |  |  |  |
| 100 |  | AcB09A |  | Installation of electric valve actuators, |  |  | piece |  | 1.000 |  |  |  |  |  |
| 101 |  | ID05E |  | Flanged gate valve or globe valve with check valve, for central heating systems, with a nominal diameter of 150 mm (KOM 160 check valve) |  |  | piece |  | 1.000 |  |  |  |  |  |
| 102 |  | VC24A |  | Elastic fan mounting, with rubber elastic mounts ( V VVGF-160 elastic mount) |  |  | piece |  | 2.000 |  |  |  |  |  |
| 103 |  | VB17A |  | AZC-type circular noise attenuator with a circumference of 800–1,600 mm (SR 160/900) |  |  | piece |  | 1.000 |  |  |  |  |  |
| 104 |  | ID05E |  | Valve with drawer or gate and check valve, flanged, for central heating systems, with a nominal diameter of 150 mm (Manual flow regulator for hydraulic balancing of the KP 160 system) |  |  | piece |  | 2.000 |  |  |  |  |  |
|  |  |  |  | Total A-14 Including wages |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 2.7. A-15 |  |  |  |  |  |  |  |  |  |  |
| 105 |  | VC01B |  | Installation of centrifugal fans, with a total weight of 50–400 kg, mounted on a metal frame (VKMS-315 axial fan) |  |  | piece |  | 1.000 |  |  |  |  |  |
| 106 |  | AcB09A |  | Installation of electric valve actuators, |  |  | piece |  | 1.000 |  |  |  |  |  |
| 107 |  | ID05H |  | Flanged gate valve or globe valve with check valve, for central heating systems, with a nominal diameter of 300 mm (KOM 315 check valve) |  |  | piece |  | 1.000 |  |  |  |  |  |
| 108 |  | VC24A |  | Elastic fan mounting, with rubber mounts (Elastic mount VVGF-315) |  |  | piece |  | 2.000 |  |  |  |  |  |
| 109 |  | VB17A |  | AZC-type circular noise attenuator with a circumference of 800–1,600 mm (SR 315/900) |  |  | piece |  | 1.000 |  |  |  |  |  |
| 110 |  | ID05E |  | Flanged gate valve or ball valve with check valve, for central heating systems, with a nominal diameter of 150 mm (Manual flow regulator for hydraulic balancing of the KP 140 system) |  |  | piece |  | 6.000 |  |  |  |  |  |
|  |  |  |  | Total A-15 Including wages |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 2.8. Ventilation system at smoke extraction |  |  |  |  |  |  |  |  |  |  |
| 111 |  | VC06E |  | Installation of direct-drive axial roof fans, with a flow rate of 5,000–37,000 m³/h and an electric motor of 0.55–11 kW (Axial fan ОСА 501-063-Н-00550/2) |  |  | piece |  | 1.000 |  |  |  |  |  |
| 112 |  | AcB09A |  | Installation of electric valve actuators, |  |  | piece |  | 1.000 |  |  |  |  |  |
| 113 |  | VC10A |  | Fitting of the air filter, with bags for dust extraction systems, fitted to the fan’s (FSA) intake ducts, for filtration, (Shut-off damper REG-L-630-N-LMV-D3LON) |  |  | piece |  | 1.000 |  |  |  |  |  |
| 114 |  | VC24A |  | Elastic fan mounting, with rubber elastic mounts (СОМ-ОСА-063) |  |  | piece |  | 2.000 |  |  |  |  |  |
| 115 |  | VC10A |  | Air filter assembly, with bags for dust extraction systems, fitted to the fan’s (FSA) intake ducts, for filtration, (KPU-1N-NZ-1700x1000 fire damper) |  |  | piece |  | 3.000 |  |  |  |  |  |
| 116 |  | AcB09A |  | Installation of electric valve actuators, |  |  | piece |  | 3.000 |  |  |  |  |  |
|  |  |  |  | Total Smoke extraction ventilation system Including wages |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | Direct costs |  |  | lei |  |  |  |  |  |  |  |
|  |  |  |  | Social fund |  |  | 24.00% |  |  |  |  |  |  |  |
|  |  |  |  | Material transport |  |  | % |  |  |  |  |  |  |  |
|  |  |  |  | Storage costs |  |  | % |  |  |  |  |  |  |  |
|  |  |  |  | Direct costs |  |  | 100.00 + |  |  |  |  |  |  |  |
|  |  |  |  | Overhead costs |  |  | % |  |  |  |  |  |  |  |
|  |  |  |  | Total |  |  | 100.00 + |  |  |  |  |  |  |  |
|  |  |  |  | Budget surplus |  |  | % |  |  |  |  |  |  |  |
|  |  |  |  | Total installation work Including wages |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 3. Plumbing works |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 3.1. AR-1 |  |  |  |  |  |  |  |  |  |  |
| 117 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a diameter of and a circular cross-section of 200 mm. (Galvanised sheet metal air ducts б=0.5 mm d-100 mm) |  |  | m² |  | 17.900 |  |  |  |  |  |
| 118 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5mm d-125mm) |  |  | m² |  | 23.160 |  |  |  |  |  |
| 119 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5 mm d-140 mm) |  |  | m² |  | 18.460 |  |  |  |  |  |
| 120 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5mm d-150mm) |  |  | m² |  | 28.260 |  |  |  |  |  |
| 121 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5mm d-160mm) |  |  | m² |  | 27.630 |  |  |  |  |  |
| 122 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5 mm d-180 mm) |  |  | m² |  | 14.700 |  |  |  |  |  |
| 123 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5mm d-200mm) |  |  | m² |  | 18.840 |  |  |  |  |  |
| 124 |  | VA19A |  | Installation of ventilation ducts at a height of 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5mm d-225mm) |  |  | m² |  | 14.130 |  |  |  |  |  |
| 125 |  | VA22B |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.5 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 1200 mm. (Galvanised sheet metal air ducts, thickness 0.5 mm, 200 x 150 mm) |  |  | m² |  | 1.000 |  |  |  |  |  |
| 126 |  | VA22B |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 1200 mm. (Galvanised sheet metal air ducts, b = 0.7 mm, 250 x 150 mm) |  |  | m² |  | 8.800 |  |  |  |  |  |
| 127 |  | VA22B |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 1,200 mm. (Galvanised sheet metal air ducts, thickness 0.7 mm, 250 x 200 mm) |  |  | m² |  | 3.600 |  |  |  |  |  |
| 128 |  | VA22B |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 1,200 mm. (Galvanised sheet metal air ducts, thickness 0.7 mm, 300 x 150 mm) |  |  | m² |  | 24.300 |  |  |  |  |  |
| 129 |  | VA22B |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 1200 mm. (Galvanised sheet metal air ducts , b=0.7 mm, 300x200 mm, 350x150 mm) |  |  | m² |  | 20.000 |  |  |  |  |  |
| 130 |  | VA22B |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 1200 mm. (Galvanised sheet metal air ducts б=0.7 мм, 400х150мм) |  |  | m² |  | 2.200 |  |  |  |  |  |
| 131 |  | VA22B |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 1,200 mm. (Galvanised sheet metal air ducts, thickness 0.7 mm, 400 × 200 mm) |  |  | m² |  | 1.000 |  |  |  |  |  |
| 132 |  | VA22B |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 1,200 mm. (Galvanised sheet metal air ducts, thickness 0.7 mm, 450 × 150 mm) |  |  | m² |  | 36.000 |  |  |  |  |  |
| 133 |  | VA22B |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 1,200 mm. (Galvanised sheet metal air ducts, thickness 0.7 mm, 500 x 150 mm) |  |  | m² |  | 2.600 |  |  |  |  |  |
| 134 |  | VA22D |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 2,000 mm. (Galvanised sheet metal air ducts, b = 0.7 mm, 550 × 150 mm) |  |  | m² |  | 15.400 |  |  |  |  |  |
| 135 |  | VA22B |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 1,200 mm. (Galvanised sheet metal air ducts, thickness 0.7 mm, 550 × 200 mm) |  |  | m² |  | 31.500 |  |  |  |  |  |
| 136 |  | VA22D |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 2,000 mm. (Galvanised sheet metal air ducts, b = 0.7 mm, 600 × 150 mm) |  |  | m² |  | 7.500 |  |  |  |  |  |
| 137 |  | VA22D |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 2000 mm. (Galvanised sheet metal air ducts, thickness 0.7 mm, 600 x 200 mm) |  |  | m² |  | 28.800 |  |  |  |  |  |
| 138 |  | VA22D |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 2000 mm. (Galvanised sheet metal air ducts, b = 0.7 mm, 600 x 250 mm) |  |  | m² |  | 13.600 |  |  |  |  |  |
| 139 |  | VA22D |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 2,000 mm. (Galvanised sheet metal air ducts, b = 0.7 mm, 600 × 600 mm) |  |  | m² |  | 7.200 |  |  |  |  |  |
| 140 |  | VA22D |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 2,000 mm. (Galvanised sheet metal air ducts, b = 0.7 mm, 650 × 200 mm) |  |  | m² |  | 1.000 |  |  |  |  |  |
| 141 |  | VA22D |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 2000 mm. (Galvanised sheet metal air ducts, thickness 0.7 mm, 650 x 250 mm) |  |  | m² |  | 10.800 |  |  |  |  |  |
| 142 |  | VA22D |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 2,000 mm. (Galvanised sheet metal air ducts, b = 0.7 mm, 700 × 250 mm) |  |  | m² |  | 3.800 |  |  |  |  |  |
| 143 |  | VA22E |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 3,600 mm. (Galvanised sheet metal air ducts, b = 0.7 mm, 700 × 400 mm) |  |  | m² |  | 8.800 |  |  |  |  |  |
| 144 |  | VA22E |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium with a perimeter of up to 3,600 mm. (Galvanised sheet metal air ducts б=0.7 мм, 800x400мм) |  |  | m² |  | 9.600 |  |  |  |  |  |
| 145 |  | VA22E |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 3600 mm. (Galvanised sheet metal air ducts, thickness 0.7 mm, 900 x 400 mm) |  |  | m² |  | 98.800 |  |  |  |  |  |
| 146 |  | VA22E |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.9 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 3,600 mm. (Galvanised sheet metal air ducts, b = 0.7 mm, 900 × 700 mm) |  |  | m² |  | 12.800 |  |  |  |  |  |
| 147 |  | VA22E |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.9 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 3,600 mm. (Galvanised sheet metal air ducts, b = 0.9 mm, 1,100 × 400 mm) |  |  | m² |  | 36.000 |  |  |  |  |  |
| 148 |  | VA05A |  | On-site installation of ready-made ALP ventilation ducts with a cross-sectional perimeter of 150–700 mm (D100 flexible air ducts) |  |  | m |  | 6.000 |  |  |  |  |  |
| 149 |  | VA05A |  | On-site installation of prefabricated ALP ventilation ducts with a cross-sectional diameter of 150–700 mm (D150 flexible air ducts) |  |  | m |  | 6.000 |  |  |  |  |  |
| 150 |  | VA05A |  | On-site installation of prefabricated ALP ventilation ducts with a cross-sectional circumference of 150–700 mm (flexible air ducts D160) |  |  | m |  | 12.000 |  |  |  |  |  |
| 151 |  | VA05A |  | On-site installation of prefabricated ALP ventilation ducts with a cross-sectional circumference of 150–700 mm (flexible air ducts D180) |  |  | m |  | 2.000 |  |  |  |  |  |
| 152 |  | VA05A |  | On-site installation of prefabricated ALP ventilation pipes, with a cross-sectional circumference of 150–700 mm ( D200) |  |  | m |  | 1.000 |  |  |  |  |  |
| 153 |  | VA05A |  | On-site installation of ready-made ALP ventilation ducts with a cross-sectional circumference of 150–700 mm (flexible air ducts D225) |  |  | m |  | 3.000 |  |  |  |  |  |
| 154 |  | IzH05A |  | Insulation of pipes using glass wool mats, Type I or Type P mineral wool sewn on one side, on galvanised wire mesh, made on site, with a thickness of 50 mm, for pipes with a circumference over the thermal insulation of less than 50 cm, inclusive (Mineral wool insulation g=30 mm, ‘Mat Prošivnoy TEKHNO-80’, with aluminium foil and mesh for mechanical strength) |  |  | m² |  | 143.000 |  |  |  |  |  |
| 155 |  | IzH05A |  | Insulation of pipes using glass wool mats, Type I or Type P mineral wool sewn onto one side of galvanised wire mesh, manufactured on site, with a thickness of 50 mm, for pipes with a circumference of 50 cm or less, inclusive (Mineral wool insulation, thickness 50 mm, ‘Mat proşivnoy TEKHNO-50’,‘Technonikol’, with aluminium foil and mesh for mechanical strength) |  |  | m² |  | 4.000 |  |  |  |  |  |
| 156 |  | CL20A |  | Ready-made ventilation grilles made of black sheet metal, with manually adjustable louvers, painted and fitted into masonry (EAV-CR-125 recirculation diffuser) |  |  | piece |  | 8.000 |  |  |  |  |  |
| 157 |  | CL20A |  | Ready-made ventilation grilles made from black sheet metal, with manually adjustable louvres, painted and fitted into the masonry (EAV-CR-150 recirculation diffuser) |  |  | piece |  | 90.000 |  |  |  |  |  |
| 158 |  | CL20A |  | Ready-made ventilation grilles made of black sheet metal, with manually adjustable louvres, painted and fitted into masonry (EAV-CR-125 recirculation diffuser for supply air) |  |  | piece |  | 37.000 |  |  |  |  |  |
| 159 |  | CL20A |  | Ready-made ventilation grilles made of black sheet metal, with manually adjustable louvres, painted and fitted into masonry (EAV-CR-150 supply and extract diffuser) |  |  | piece |  | 24.000 |  |  |  |  |  |
| 160 |  | CL20A |  | Ready-made ventilation grilles made of black sheet metal, with manually adjustable louvers, painted and fitted into masonry (Rectangular multi-directional ceiling diffuser complete with PDZ-2 side-connection air distribution box, AQN 300×300) |  |  | piece |  | 4.000 |  |  |  |  |  |
| 161 |  | CL20A |  | Ready-made ventilation grilles made of black sheet metal, with manually adjustable louvers, painted and fitted into masonry (Rectangular multi-directional ceiling diffuser supplied complete with PDZ-2 side-connection air distribution box, AQN 375×375) |  |  | piece |  | 5.000 |  |  |  |  |  |
| 162 |  | VC34A |  | Manufacture and installation of support and anchoring devices for equipment, ducts, special components, etc., made from profiled steel, with a weight per piece of up to 5 kg |  |  | kg |  | 1,750.000 |  |  |  |  |  |
| 163 |  | CN20B |  | Interior or exterior paintwork applied to metal joinery using alkyd enamel in 2 coats, including primer (Paint for substrates) |  |  | m² |  | 63.000 |  |  |  |  |  |
|  |  |  |  | Total AR-1 Including wages |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 3.2. AR-2 |  |  |  |  |  |  |  |  |  |  |
| 164 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a diameter of and a circular cross-section of 200 mm. (Galvanised sheet metal air ducts б=0.5 mm d-100 mm) |  |  | m² |  | 8.800 |  |  |  |  |  |
| 165 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5mm d-125mm) |  |  | m² |  | 21.200 |  |  |  |  |  |
| 166 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5 mm d-140 mm) |  |  | m² |  | 25.940 |  |  |  |  |  |
| 167 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5mm d-150mm) |  |  | m² |  | 30.150 |  |  |  |  |  |
| 168 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5mm d-160mm) |  |  | m² |  | 14.570 |  |  |  |  |  |
| 169 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5 mm d-180 mm) |  |  | m² |  | 16.390 |  |  |  |  |  |
| 170 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5mm d-200mm) |  |  | m² |  | 19.330 |  |  |  |  |  |
| 171 |  | VA19A |  | Installation of ventilation ducts at a height of 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5mm d-225mm) |  |  | m² |  | 14.840 |  |  |  |  |  |
| 172 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5 mm d-250 mm) |  |  | m² |  | 0.785 |  |  |  |  |  |
| 173 |  | VA22B |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.5 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 1200 mm. (Galvanised sheet metal air ducts, thickness 0.5 mm, 200 x 150 mm) |  |  | m² |  | 9.100 |  |  |  |  |  |
| 174 |  | VA22B |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.5 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 1,200 mm. (Galvanised sheet metal air ducts, b = 0.5 mm, 250 x 150 mm) |  |  | m² |  | 12.000 |  |  |  |  |  |
| 175 |  | VA22B |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 1,200 mm. (Galvanised sheet metal air ducts, thickness 0.7 mm, 300 x 150 mm) |  |  | m² |  | 37.800 |  |  |  |  |  |
| 176 |  | VA22B |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 1,200 mm. (Galvanised sheet metal air ducts, thickness 0.7 mm, 350 x 150 mm) |  |  | m² |  | 15.000 |  |  |  |  |  |
| 177 |  | VA22B |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.6 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 1200 mm. (Galvanised sheet metal air ducts, thickness 0.6 mm, 400 x 150 mm) |  |  | m² |  | 49.500 |  |  |  |  |  |
| 178 |  | VA22B |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.5 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 1,200 mm. (Galvanised sheet metal air ducts, thickness 0.5 mm, 450 x 150 mm) |  |  | m² |  | 22.800 |  |  |  |  |  |
| 179 |  | VA22B |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.5 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 1,200 mm. (Galvanised sheet metal air ducts, thickness 0.5 mm, 450 × 200 mm) |  |  | m² |  | 3.900 |  |  |  |  |  |
| 180 |  | VA22B |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 1,200 mm. (Galvanised sheet metal air ducts, thickness 0.7 mm, 500 x 150 mm) |  |  | m² |  | 39.000 |  |  |  |  |  |
| 181 |  | VA22D |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 2000 mm. (Galvanised sheet metal air ducts, thickness 0.7 mm, 500 × 200 mm) |  |  | m² |  | 8.400 |  |  |  |  |  |
| 182 |  | VA22D |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 2,000 mm. (Galvanised sheet metal air ducts, b = 0.7 mm, 500 × 250 mm) |  |  | m² |  | 1.500 |  |  |  |  |  |
| 183 |  | VA22D |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 2,000 mm. (Galvanised sheet metal air ducts, b = 0.7 mm, 550 × 150 mm) |  |  | m² |  | 19.600 |  |  |  |  |  |
| 184 |  | VA22D |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 2,000 mm. (Galvanised sheet metal air ducts , thickness 0.7 mm, 550 × 250 mm) |  |  | m² |  | 8.000 |  |  |  |  |  |
| 185 |  | VA22D |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 2000 mm. (Galvanised sheet metal air ducts, b = 0.7 mm, 600 x 250 mm) |  |  | m² |  | 13.600 |  |  |  |  |  |
| 186 |  | VA22D |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 2,000 mm. (Galvanised sheet metal air ducts, b = 0.7 mm, 650 × 150 mm) |  |  | m² |  | 1.600 |  |  |  |  |  |
| 187 |  | VA22D |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 2000 mm. (Galvanised sheet metal air ducts, thickness 0.7 mm, 650 x 250 mm) |  |  | m² |  | 5.100 |  |  |  |  |  |
| 188 |  | VA22E |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 3,600 mm. (Galvanised sheet metal air ducts, b = 0.7 mm, 700 × 600 mm) |  |  | m² |  | 13.000 |  |  |  |  |  |
| 189 |  | VA22E |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 3600 mm. (Galvanised sheet metal air ducts, thickness 0.7 mm, 750 x 400 mm) |  |  | m² |  | 9.200 |  |  |  |  |  |
| 190 |  | VA22E |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 3,600 mm. (Galvanised sheet metal air ducts, b = 0.7 mm, 900 x 700 mm) |  |  | m² |  | 19.200 |  |  |  |  |  |
| 191 |  | VA22E |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.9 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 3,600 mm. (Galvanised sheet metal air ducts, b = 0.9 mm, 1,000 x 400 mm) |  |  | m² |  | 179.200 |  |  |  |  |  |
| 192 |  | VA22E |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.9 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 3,600 mm. (Galvanised sheet metal air ducts, b = 0.9 mm, 1,050 x 400 mm) |  |  | m² |  | 43.500 |  |  |  |  |  |
| 193 |  | VA05A |  | On-site installation of prefabricated ALP ventilation ducts with a cross-sectional diameter of 150–700 mm (D140 flexible air ducts) |  |  | m |  | 1.000 |  |  |  |  |  |
| 194 |  | VA05A |  | On-site installation of prefabricated ALP ventilation ducts with a cross-sectional diameter of 150–700 mm (D150 flexible air ducts) |  |  | m |  | 9.000 |  |  |  |  |  |
| 195 |  | VA05A |  | On-site installation of prefabricated ALP ventilation ducts with a cross-sectional circumference of 150–700 mm (flexible air ducts D160) |  |  | m |  | 7.000 |  |  |  |  |  |
| 196 |  | VA05A |  | On-site installation of prefabricated ALP ventilation ducts with a cross-sectional circumference of 150–700 mm (flexible air ducts D180) |  |  | m |  | 2.000 |  |  |  |  |  |
| 197 |  | VA05A |  | On-site installation of prefabricated ALP ventilation ducts with a cross-sectional circumference of 150–700 mm (flexible air ducts D200) |  |  | m |  | 2.000 |  |  |  |  |  |
| 198 |  | VA05A |  | On-site installation of ready-made ALP ventilation ducts with a cross-sectional circumference of 150–700 mm (flexible air ducts D225) |  |  | m |  | 4.000 |  |  |  |  |  |
| 199 |  | IzH05A |  | Insulation of ducts with glass wool mats, type I or type P mineral wool sewn on one side, onto galvanised wire mesh, manufactured on site, with a thickness of 50 mm, for pipes with a circumference ( ) over the thermal insulation of less than or equal to 50 cm (Mineral wool insulation g=30 mm, ‘Mat Prošivnoy TEKHNO-80’, with aluminium foil and mesh for mechanical strength) |  |  | m² |  | 224.000 |  |  |  |  |  |
| 200 |  | IzH05A |  | Insulation of pipes using glass wool mats, Type I or Type P mineral wool sewn on one side, on galvanised wire mesh, manufactured on site, with a thickness of 50 mm, for pipes with a circumference, including the thermal insulation, of less than 50 cm (Mineral wool insulation, thickness 50 mm, ‘Mat Prošivnoy TEKHNO-50’, with aluminium foil and mesh for mechanical strength) |  |  | m² |  | 4.000 |  |  |  |  |  |
| 201 |  | CL20A |  | Ready-made ventilation grilles made of black sheet metal, with manually adjustable louvres, painted and fitted into masonry (EAV-CR-125 adjustable circular diffuser for supply air) |  |  | piece |  | 16.000 |  |  |  |  |  |
| 202 |  | CL20A |  | Ready-made ventilation grilles made from black sheet metal, with manually adjustable louvres, painted and fitted into the masonry (EAV-CR-150 adjustable recirculation diffuser) |  |  | piece |  | 88.000 |  |  |  |  |  |
| 203 |  | CL20A |  | Ready-made ventilation grilles made of black sheet metal, with manually adjustable louvres, painted and fitted into masonry (EAV-CR-125 recirculation diffuser for exhaust) |  |  | piece |  | 35.000 |  |  |  |  |  |
| 204 |  | CL20A |  | Ready-made ventilation grilles made of black sheet metal, with manually adjustable louvres, painted and fitted into masonry (EAV-CR-150 supply and extract diffuser) |  |  | piece |  | 35.000 |  |  |  |  |  |
| 205 |  | CL20A |  | Ready-made ventilation grilles made of black sheet metal, with manually adjustable louvers, painted and fitted into masonry ( -complete rectangular multi-directional ceiling diffuser with PDZ-2 side-connection air distribution box, AQN 300×300) |  |  | piece |  | 2.000 |  |  |  |  |  |
| 206 |  | CL20A |  | Ready-made ventilation grilles made of black sheet metal, with manually adjustable louvers, painted and fitted into masonry (Rectangular multi-directional ceiling diffuser supplied complete with PDZ-2 side-connection air distribution box, AQN 375×375) |  |  | piece |  | 8.000 |  |  |  |  |  |
| 207 |  | VC34A |  | Manufacture and installation of support and anchoring devices for equipment, ducts, special components, etc., made from profiled steel, with a weight per piece of up to 5 kg |  |  | kg |  | 1,950.000 |  |  |  |  |  |
| 208 |  | CN20B |  | Interior or exterior paintwork applied to metal joinery using alkyd enamel in 2 coats, including primer (Paint for substrates) |  |  | m² |  | 70.200 |  |  |  |  |  |
|  |  |  |  | Total AR-2 Including wages |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 3.3. AR-11 |  |  |  |  |  |  |  |  |  |  |
| 209 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5mm d-200mm). |  |  | m² |  | 1.890 |  |  |  |  |  |
| 210 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.6 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.6mm d-250mm) |  |  | m² |  | 4.710 |  |  |  |  |  |
| 211 |  | VA20B |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised or aluminium sheet, 0.6 mm thick, with a circular cross-sectional diameter of up to 800 mm (Air ducts made of galvanised sheet б=0.6 mm d-280 mm) |  |  | m² |  | 7.040 |  |  |  |  |  |
| 212 |  | VA20B |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.6 mm thick galvanised sheet metal or aluminium, with a circular cross-sectional diameter of up to 800 mm (galvanised sheet metal air ducts б=0.6 mm d-315 mm) |  |  | m² |  | 39.570 |  |  |  |  |  |
| 213 |  | VA22B |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 1200 mm. (Galvanised sheet metal air ducts б=0.7 мм, 300x250мм) |  |  | m² |  | 14.300 |  |  |  |  |  |
| 214 |  | VA22B |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 1,200 mm. (Galvanised sheet metal air ducts, thickness 0.7 mm, 400 × 200 mm) |  |  | m² |  | 26.400 |  |  |  |  |  |
| 215 |  | IzH05A |  | Insulation of pipes using glass wool mats, Type I or Type P mineral wool sewn on one side, on galvanised wire mesh, made on site, with a thickness of 50 mm, for pipes with a circumference over the thermal insulation of less than 50 cm, inclusive (Mineral wool insulation g=30 mm, ‘Mat Prošivnoy TEKHNO-80’, with aluminium foil and mesh for mechanical strength) |  |  | m² |  | 32.000 |  |  |  |  |  |
| 216 |  | IzH05A |  | Insulation of pipes using glass wool mats, Type I or Type P mineral wool sewn on one side, on galvanised wire mesh, manufactured on site, with a thickness of 50 mm, for pipes with a circumference, including the thermal insulation, of less than 50 cm (Mineral wool insulation, thickness 50 mm, ‘Mat Prošivnoy TEKHNO-50’, with aluminium foil and mesh for mechanical strength) |  |  | m² |  | 9.000 |  |  |  |  |  |
| 217 |  | CL20A |  | Ready-made ventilation grilles made of black sheet metal, with manually adjustable louvres, painted and fitted into masonry (Circular ventilation grille with the exact diameter of the BMC 800x100 duct) |  |  | piece |  | 9.000 |  |  |  |  |  |
| 218 |  | VC34A |  | Manufacture and installation of support and anchoring devices for equipment, ducts, special components, etc., made from profiled steel, with a weight per piece of up to 5 kg |  |  | kg |  | 280.000 |  |  |  |  |  |
| 219 |  | CN20B |  | Interior or exterior paintwork applied to metal joinery using alkyd enamel in 2 coats, including primer (Paint for substrates) |  |  | m² |  | 10.560 |  |  |  |  |  |
|  |  |  |  | Total AR-11 Including wages |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 3.4. AR-12 |  |  |  |  |  |  |  |  |  |  |
| 220 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5mm d-150mm) |  |  | m² |  | 4.710 |  |  |  |  |  |
| 221 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5mm d-160mm) |  |  | m² |  | 4.530 |  |  |  |  |  |
| 222 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5mm d-225mm) |  |  | m² |  | 7.070 |  |  |  |  |  |
| 223 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.6 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.6 mm d-250 mm) |  |  | m² |  | 6.280 |  |  |  |  |  |
| 224 |  | VA22B |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 1200 mm. (Galvanised sheet metal air ducts б=0.7 мм, 300x250мм) |  |  | m² |  | 4.400 |  |  |  |  |  |
| 225 |  | VA22B |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 1,200 mm. (Galvanised sheet metal air ducts, thickness 0.7 mm, 400 × 250 mm) |  |  | m² |  | 6.500 |  |  |  |  |  |
| 226 |  | VA22D |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 2,000 mm. (Galvanised sheet metal air ducts, b = 0.7 mm, 400 × 400 mm) |  |  | m² |  | 8.000 |  |  |  |  |  |
| 227 |  | VA22D |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 2,000 mm. (Galvanised sheet metal air ducts, b = 0.7 mm, 500 × 250 mm) |  |  | m² |  | 4.500 |  |  |  |  |  |
| 228 |  | VA22D |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 2000 mm. (Galvanised sheet metal air ducts, thickness 0.7 mm, 500 x 300 mm) |  |  | m² |  | 6.400 |  |  |  |  |  |
| 229 |  | VA22D |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 2,000 mm. (Galvanised sheet metal air ducts, b = 0.7 mm, 500 × 400 mm) |  |  | m² |  | 91.800 |  |  |  |  |  |
| 230 |  | VA22D |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised or aluminium sheet , with a perimeter of up to 2000 mm. (Galvanised sheet metal air ducts, b = 0.7 mm, 600 x 300 mm) |  |  | m² |  | 46.000 |  |  |  |  |  |
| 231 |  | VA22D |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 2000 mm. (Galvanised sheet metal air ducts, b = 0.7 mm, 600 x 400 mm) |  |  | m² |  | 200.000 |  |  |  |  |  |
| 232 |  | VA05A |  | On-site installation of ready-made ALP ventilation ducts with a cross-sectional circumference of 150–700 mm (flexible air ducts D225) |  |  | m |  | 2.000 |  |  |  |  |  |
| 233 |  | VA05A |  | On-site installation of prefabricated ALP ventilation ducts with a cross-sectional circumference of 150–700 mm (flexible air ducts D250) |  |  | m |  | 3.000 |  |  |  |  |  |
| 234 |  | IzH05A |  | Insulation of pipes using glass wool mats, Type I or Type P mineral wool sewn on one side, on galvanised wire mesh, made on site, with a thickness of 50 mm, for pipes with a circumference over the thermal insulation of less than 50 cm, inclusive (Mineral wool insulation g=30 mm, ‘Mat Prošivnoy TEKHNO-80’, with aluminium foil and mesh for mechanical strength) |  |  | m² |  | 78.000 |  |  |  |  |  |
| 235 |  | IzH05A |  | Insulation of pipes using glass wool mats, Type I or Type P mineral wool sewn on one side, on galvanised wire mesh, manufactured on site, with a thickness of 50 mm, for pipes with a circumference, including the thermal insulation, of less than 50 cm (Mineral wool insulation, thickness 50 mm, ‘Mat Prošivnoy TEKHNO-50’, with aluminium foil and mesh for mechanical strength) |  |  | m² |  | 11.000 |  |  |  |  |  |
| 236 |  | CL20A |  | Ready-made ventilation grilles made of black sheet metal, with manually adjustable louvers, painted with ‘ ’ and installed in masonry (CFC-+RC 300 circular diffuser) |  |  | piece |  | 2.000 |  |  |  |  |  |
| 237 |  | CL20A |  | Ready-made ventilation grilles made of black sheet metal, with manually adjustable louvers, painted and fitted into masonry (CFC-+RC 150 circular diffuser) |  |  | piece |  | 2.000 |  |  |  |  |  |
| 238 |  | CL20A |  | Ready-made ventilation grilles made from black sheet metal, with manually adjustable louvers, painted and fitted into the masonry (Rectangular multi-directional ceiling diffuser supplied complete with PDZ-2 air distribution box with side connection, AQN 600x600) |  |  | piece |  | 9.000 |  |  |  |  |  |
| 239 |  | VC34A |  | Manufacture and installation of support and anchoring devices for equipment, ducts, special components, etc., made from profiled steel, with a weight per piece of up to 5 kg |  |  | kg |  | 400.000 |  |  |  |  |  |
| 240 |  | CN20B |  | Interior or exterior paintwork applied to metal joinery using alkyd enamel in 2 coats, including primer (Paint for substrates) |  |  | m² |  | 15.300 |  |  |  |  |  |
|  |  |  |  | Total AR-12 Including wages |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 3.5. A-13 |  |  |  |  |  |  |  |  |  |  |
| 241 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5 mm d-100 mm) |  |  | m² |  | 4.710 |  |  |  |  |  |
| 242 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5mm d-125mm) |  |  | m² |  | 2.750 |  |  |  |  |  |
| 243 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5 mm d-140 mm) |  |  | m² |  | 1.760 |  |  |  |  |  |
| 244 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5mm d-150mm) |  |  | m² |  | 5.190 |  |  |  |  |  |
| 245 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5mm d-160mm) |  |  | m² |  | 3.020 |  |  |  |  |  |
| 246 |  | IzH05A |  | Insulation of pipes using glass wool mats, Type I or Type P mineral wool sewn on one side, on galvanised wire mesh, made on site, with a thickness of 50 mm, for pipes with a circumference over the thermal insulation of less than 50 cm, inclusive (Mineral wool insulation g=30 mm, ‘Mat Prošivnoy TEKHNO-80’, with aluminium foil and mesh for mechanical strength) |  |  | m² |  | 6.000 |  |  |  |  |  |
| 247 |  | CL20A |  | Ready-made ventilation grilles made of black sheet metal, with manually adjustable louvers, painted and fitted into masonry (EAV+CM-100 supply and extract diffuser) |  |  | piece |  | 6.000 |  |  |  |  |  |
| 248 |  | CL20A |  | Ready-made ventilation grilles made of black sheet metal, with manually adjustable louvers, painted and fitted into masonry (Umberla d-160) |  |  | piece |  | 1.000 |  |  |  |  |  |
| 249 |  | VC34A |  | Manufacture and installation of support and anchoring devices for equipment, ducts, special components, etc., made from section steel, with a unit weight ( ) of up to 5 kg |  |  | kg |  | 130.000 |  |  |  |  |  |
| 250 |  | CN20B |  | Interior or exterior paintwork applied to metal joinery using alkyd enamel in 2 coats, including primer (Paint for substrates) |  |  | m² |  | 4.680 |  |  |  |  |  |
|  |  |  |  | Total A-13 Including wages |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 3.6. A-14 |  |  |  |  |  |  |  |  |  |  |
| 251 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5mm d-125mm) |  |  | m² |  | 1.180 |  |  |  |  |  |
| 252 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5mm d-150mm) |  |  | m² |  | 1.890 |  |  |  |  |  |
| 253 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5mm d-160mm) |  |  | m² |  | 5.030 |  |  |  |  |  |
| 254 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5mm d-200mm) |  |  | m² |  | 0.630 |  |  |  |  |  |
| 255 |  | VA22B |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of up to 1200 mm. (Galvanised sheet metal air ducts, b = 0.7 mm, 250 x 150 mm) |  |  | m² |  | 21.600 |  |  |  |  |  |
| 256 |  | VA05A |  | On-site installation of ready-made ALP ventilation s, with a cross-sectional perimeter of 150–700 mm (Flexible air ducts D160) |  |  | m |  | 2.000 |  |  |  |  |  |
| 257 |  | IzH05A |  | Insulation of pipes using glass wool mats, Type I or Type P mineral wool sewn on one side, on galvanised wire mesh, made on site, with a thickness of 50 mm, for pipes with a circumference over the thermal insulation of less than 50 cm, inclusive (Mineral wool insulation g=30 mm, ‘Mat Prošivnoy TEKHNO-80’, with aluminium foil and mesh for mechanical strength) |  |  | m² |  | 10.000 |  |  |  |  |  |
| 258 |  | CL20A |  | Ready-made ventilation grilles made of black sheet metal, with manually adjustable louvres, painted and fitted into masonry (EAV-CR-125 recirculation diffuser for exhaust) |  |  | piece |  | 6.000 |  |  |  |  |  |
| 259 |  | CL20A |  | Ready-made ventilation grilles made of black sheet metal, with manually adjustable louvers, painted and fitted into masonry (Umberla d-160) |  |  | piece |  | 1.000 |  |  |  |  |  |
| 260 |  | VC34A |  | Manufacture and installation of support and anchoring devices for equipment, ducts, special components, etc., made from profiled steel, with a weight per piece of up to 5 kg |  |  | kg |  | 130.000 |  |  |  |  |  |
| 261 |  | CN20B |  | Interior or exterior paintwork applied to metal joinery using alkyd enamel in 2 coats, including primer (Paint for substrates) |  |  | m² |  | 4.500 |  |  |  |  |  |
|  |  |  |  | Total A-14 Including wages |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 3.7. A-15 |  |  |  |  |  |  |  |  |  |  |
| 262 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5 mm d-100 mm) |  |  | m² |  | 1.890 |  |  |  |  |  |
| 263 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5mm d-125mm) |  |  | m² |  | 2.748 |  |  |  |  |  |
| 264 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5 mm d-140 mm) |  |  | m² |  | 13.630 |  |  |  |  |  |
| 265 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.5 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.5 mm d-180 mm) |  |  | m² |  | 4.530 |  |  |  |  |  |
| 266 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.6 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.6mm d-250mm) |  |  | m² |  | 3.140 |  |  |  |  |  |
| 267 |  | VA19A |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of galvanised sheet metal or aluminium, 0.6 mm thick, with a circular cross-sectional diameter of 200 mm. (Galvanised sheet metal air ducts б=0.6mm d-315mm) |  |  | m² |  | 3.960 |  |  |  |  |  |
| 268 |  | IzH05A |  | Insulation of pipes using glass wool mats, Type I or Type P mineral wool sewn on one side, on galvanised wire mesh, made on site, with a thickness of 50 mm, for pipes with a circumference including the thermal insulation of 50 cm or less (Mineral wool insulation, thickness 30 mm, ‘Mat Prošivnoy TEKHNO-80’, with aluminium foil and mesh for mechanical strength) |  |  | m² |  | 8.000 |  |  |  |  |  |
| 269 |  | CL20A |  | Ready-made ventilation grilles made of black sheet metal, with manually adjustable louvers, painted and fitted into masonry (EAV+CM-100 supply and extract diffuser) |  |  | piece |  | 24.000 |  |  |  |  |  |
| 270 |  | CL20A |  | Ready-made ventilation grilles made of black sheet metal, with manually adjustable louvers, painted and fitted into masonry (Umberla d-315) |  |  | piece |  | 1.000 |  |  |  |  |  |
| 271 |  | VC34A |  | Manufacture and installation of support and anchoring devices for equipment, ducts, special components, etc., made from profiled steel, with a weight per piece of up to 5 kg |  |  | kg |  | 180.000 |  |  |  |  |  |
| 272 |  | CN20B |  | Interior or exterior paintwork applied to metal joinery using alkyd enamel in 2 coats, including primer (Paint for substrates) |  |  | m² |  | 6.480 |  |  |  |  |  |
|  |  |  |  | Total A-15 Including wages |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 3.8. Fresh air duct for AR1-AR2, AR-11, AR-12 |  |  |  |  |  |  |  |  |  |  |
| 273 |  | VA22F |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.7 mm thick galvanised sheet metal or aluminium, with a perimeter of 4000 mm. (Galvanised sheet metal air ducts, thickness 0.9 mm, 1600 x 800) |  |  | m² |  | 14.400 |  |  |  |  |  |
| 274 |  | IzH05A |  | Insulation of pipes using glass wool mats, Type I or Type P mineral wool sewn on one side, on galvanised wire mesh, made on site, with a thickness of 50 mm, for pipes with a circumference over the thermal insulation of less than 50 cm, inclusive (Mineral wool insulation g=30 mm, ‘Mat Prošivnoy TEKHNO-80’, with aluminium foil and mesh for mechanical strength) |  |  | m² |  | 16.000 |  |  |  |  |  |
| 275 |  | CL20A |  | Ready-made ventilation grilles made from black sheet metal, with manually adjustable louvres, painted and fitted into masonry (SS-A 1000x600 external metal grille with louvres for air discharge) |  |  | piece |  | 3.000 |  |  |  |  |  |
| 276 |  | VC34A |  | Manufacture and installation of support and anchoring devices for equipment, ducts, special components, etc., made from profiled steel, with a weight per piece of up to 5 kg |  |  | kg |  | 10.000 |  |  |  |  |  |
| 277 |  | CN20B |  | Interior or exterior paintwork applied to metal joinery using alkyd enamel in 2 coats, including primer (Paint for substrates) |  |  | m² |  | 0.400 |  |  |  |  |  |
|  |  |  |  | Total Fresh air duct for AR1-AR2, AR-11, AR-12 Including labour |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 3.9. Smoke extraction ventilation system |  |  |  |  |  |  |  |  |  |  |
| 278 |  | VA20B |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 0.8 mm thick galvanised sheet metal or aluminium, with a circular cross-sectional diameter of up to 800 mm (galvanised sheet metal air ducts, thickness 0.8 mm, diameter 630 mm) |  |  | m² |  | 7.913 |  |  |  |  |  |
| 279 |  | VA22F |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 1.0 mm thick galvanised sheet metal or aluminium, with a perimeter of 4,000 mm. (Galvanised sheet metal air ducts, thickness 1.0 mm, 1,300 × 600 mm) |  |  | m² |  | 34.200 |  |  |  |  |  |
| 280 |  | VA22F |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 1.0 mm thick galvanised sheet metal or aluminium, with a perimeter of 4,000 mm. (Galvanised sheet metal air ducts, b = 1.0 mm, 1,700 × 450 mm) |  |  | m² |  | 86.000 |  |  |  |  |  |
| 281 |  | VA22F |  | Installation of ventilation ducts at a height of up to 3 m from the floor, made of 1.0 mm thick galvanised or aluminium sheet , with a perimeter of 4,000 mm. (Galvanised sheet metal air ducts, b = 1.0 mm, 1,700 × 1,000 mm) |  |  | m² |  | 10.800 |  |  |  |  |  |
| 282 |  | IzH05A |  | Insulation of pipes using glass wool mats, Type I or Type P mineral wool sewn on one side, on galvanised wire mesh, made on site, with a thickness of 50 mm, for pipes with a circumference over the thermal insulation of less than 50 cm, inclusive (Mineral wool insulation g=30 mm, ‘Mat Prošivnoy TEKHNO-80’, with aluminium foil and mesh for mechanical strength) |  |  | m² |  | 148.000 |  |  |  |  |  |
| 283 |  | VC34A |  | Manufacture and installation of support and anchoring devices for equipment, ducts, special components, etc., made from profiled steel, with a weight per piece of up to 5 kg |  |  | kg |  | 100.000 |  |  |  |  |  |
| 284 |  | CN20B |  | Interior or exterior paintwork applied to metal joinery using alkyd enamel in 2 coats, including primer (Paint for substrates) |  |  | m² |  | 3.200 |  |  |  |  |  |
|  |  |  |  | Total Smoke extraction ventilation system Including labour costs |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | Direct costs |  |  | lei |  |  |  |  |  |  |  |
|  |  |  |  | Social fund |  |  | 24.00% |  |  |  |  |  |  |  |
|  |  |  |  | Material transport |  |  | % |  |  |  |  |  |  |  |
|  |  |  |  | Storage costs |  |  | % |  |  |  |  |  |  |  |
|  |  |  |  | Direct costs |  |  | 100.00 + |  |  |  |  |  |  |  |
|  |  |  |  | Overhead costs |  |  | % |  |  |  |  |  |  |  |
|  |  |  |  | Total |  |  | 100.00 + |  |  |  |  |  |  |  |
|  |  |  |  | Budget surplus |  |  | % |  |  |  |  |  |  |  |
|  |  |  |  | Total Plumbing works Including wages |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | Total quote: Including wages |  |  |  |  |  |  |  |  |  |  |

| Prepared by |  |
| --- | --- |
| (position, signature, surname, first name) |  |
| Verified |  |
| (position, signature, surname, first name) |  |