## ANNEX 4: TECHNICAL RESPONSIVENESS TABLE

Bidders are requested to complete this form, sign it and return it as part of their quotation along with Annex 2 Quotation Submission Form. The Bidder shall fill in this form in accordance with the instructions indicated. No alterations to its format shall be permitted and no substitutions shall be accepted.

| Name of Bidder: | Click or tap here to enter text. |  |
| --- | --- | --- |
| RFQ reference: | RfQ26/03352: Installation of photovoltaic system in Holercani, Dubasari | Date: Click or tap to enter a date. |

Bidders shall provide all the applicable technical data of the materials proposed to demonstrate compliance with technical specifications included in Section 5: Schedule of Requirements; failing to do so may result in the bid being rejected. Corresponding documentation shall form part of the bidder’s offer. You may also provide brochures for the offered equipment; in case it is available.

| No. | Technical parameters/characteristics for proposed materials | Requested characteristics | Quantity, pcs | Bidder’s response |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Compliance with technical specifications |  | Technical Compliance (indicate details of proposed materials) |
|  |  |  |  | Yes, we comply | No, we cannot comply (indicate discrepancies) |  |
| Three Phase Hybrid Inverter (80KW) |  | Quantity – 1 pc |  |  |  |  |
| 1 | Battery Input Data |  |  |  |  |  |
|  | Battery Type | Lithium-ion |  |  |  |  |
|  | Battery Voltage Range (V) | Min: 160 – Max: 1000 |  |  |  |  |
|  | Max. Charging Current (A) | 80+80 |  |  |  |  |
|  | Max. Discharging Current (A) | 80+80 |  |  |  |  |
|  | Charging Strategy for Li-ion Battery | Self-adaption to BMS |  |  |  |  |
|  | Number of Battery Input | 2 |  |  |  |  |
| 2 | PV String Input Data |  |  |  |  |  |
|  | Max. PV Input Voltage (V) | 1000 |  |  |  |  |
|  | Start-up Voltage (V) | 100-200 |  |  |  |  |
|  | MPPT Voltage Range (V) | 150-850 |  |  |  |  |
|  | Rated PV Input Voltage (V) | 500-1000 |  |  |  |  |
| 3 | AC Input/Output Data |  |  |  |  |  |
|  | Grid Connection Form | 3L+N+PE |  |  |  |  |
| 4 | Equipment Protection |  |  |  |  |  |
|  | Protection | manufacturer-provided |  |  |  |  |
|  | Surge Protection Level | TYPE II(DC), TYPE II(AC) |  |  |  |  |
| 5 | Interface |  |  |  |  |  |
|  | Communication Interface | RS485/RS232/CAN |  |  |  |  |
|  | Monitor Mode | GPRS/WIFI/Bluetooth/ 4G/LAN(optional) |  |  |  |  |
| 6 | General Data |  |  |  |  |  |
|  | Operating Temperature Range (℃) | -40 to +60°C, >45°C Derating |  |  |  |  |
|  | Permissible Ambient Humidity | 0-100% |  |  |  |  |
|  | Ingress Protection(IP) Rating | IP 65 |  |  |  |  |
|  | Inverter Topology | Non-Isolated |  |  |  |  |
|  | Over Voltage Category | OVC II(DC), OVC III(AC) |  |  |  |  |
|  | Grid Regulation | IEC 61727, IEC 62116, CEI 0-21, EN 50549, NRS 097, RD 140, UNE 217002, OVE-Richtlinie R25, G99, VDE-AR-N 4105 |  |  |  |  |
|  | Safety / EMC Standard | IEC/EN 61000-6-1/2/3/4, IEC/EN 62109-1, IEC/EN 62109-2 |  |  |  |  |
|  | Warranty | Minimum 5 Years |  |  |  |  |
| Photovoltaic panel |  |  | Quantity – 120 pcs |  |  |  |
| 1 | General Ratings |  |  |  |  |  |
|  | Power Output | Minimum 700W |  |  |  |  |
|  | Efficiency | Minimum 23% |  |  |  |  |
|  | Operational Temperature | -40°C - +85°C |  |  |  |  |
|  | Maximum System Voltage | 1500V DC |  |  |  |  |
| 2 | Mechanical Data |  |  |  |  |  |
|  | Cell Type | Monocrystalline |  |  |  |  |
|  | Junction Box | IP 68 rated |  |  |  |  |
|  | Connector | MC4 Compatible |  |  |  |  |
|  | Cable | Minimum 4 mm², minimum 1000V, direct current |  |  |  |  |
|  | Snow Load | Minimum 350 kg/m2 |  |  |  |  |
|  | Warranty | Minimum 10 Years for equipment |  |  |  |  |
| Electricity meter (System operator-approved) |  |  | Quantity – 1 pc |  |  |  |
| 1 | Electrical Parameters |  |  |  |  |  |
|  | Connection Type | Indirect connection via Current Transformers (CT) |  |  |  |  |
|  | Nominal Voltage (U n) | 3 × 220/380 V up to 3 × 230/400 V |  |  |  |  |
|  | Nominal Current (I n / I ref) | 5 A |  |  |  |  |
| 2 | Accuracy & Measurement Classes |  |  |  |  |  |
|  | Active/Reactive Energy (Bidirectional - Import/Export) | Class 0.5 – 1.0 (IEC 62053-22, IEC 62053-21) |  |  |  |  |
| 3 | Communication & Modem Modules |  |  |  |  |  |
|  | Integrated Modem Type | 4G LTE / 3G / GSM/GPRS or NB-IoT / LTE-M (with fallback to 2G) for remote automated meter reading (AMR), compatible with proposed electricity meter |  |  |  |  |
|  | Local Interface Built-in | RS-485 serial port and an Optical IR port (IEC 62056-21) for local readouts |  |  |  |  |
|  | Supported Protocols | DLMS/COSEM, Modbus RTU, or IEC 870-5-102 |  |  |  |  |
|  | Antenna Connection | compatible with the data transmission system and the electricity meter |  |  |  |  |
| 4 | Mechanical & Environmental Specifications |  |  |  |  |  |
|  | Operating Temperature | -40°C to +70°C |  |  |  |  |
|  | Relative Humidity Limit | non-condensing |  |  |  |  |
|  | Meter cabinet | In accordance with the connection permit and execution project |  |  |  |  |
|  | Warranty | Minimum 5 Years |  |  |  |  |
| Electrical energy storage system (LiFePO4 160–1000V) |  |  | Quantity – 1 pc |  |  |  |
| 1 | General specifications |  |  |  |  |  |
|  | System type | Modular electrical energy storage system, fully equipped |  |  |  |  |
|  | Battery technology | LiFePO4/LFP or equivalent technology in terms of safety and lifespan |  |  |  |  |
|  | Compatibility | full compatibility with the provided inverter (80 KW) in the project or with the accepted equivalent inverter |  |  |  |  |
|  | Confirmation of compatibility | official manufacturer's document, compatibility list or technical declaration assumed by the tenderer and manufacturer |  |  |  |  |
|  | BMS system | Integrated, with cell balancing and protection |  |  |  |  |
|  | Communication | CAN, RS485 or protocol accepted by the inverter |  |  |  |  |
|  | Minimum depth of discharge | 90% |  |  |  |  |
|  | Life span | Minimum 6,000 cycles |  |  |  |  |
|  | Protections | Overvoltage, undervoltage, overcurrent, short circuit, excessive temperature, excessive discharge and cell imbalance |  |  |  |  |
|  | Protection degree | Minimum IP54 for outdoor installation |  |  |  |  |
|  | Temperature range for module | the operating range will include at least the range –20°C…+50°C; any power limitations will be declared |  |  |  |  |
|  | Fire safety | detection and protection system appropriate to the type and size of the equipment, according to the manufacturer's solution |  |  |  |  |
|  | Warranty | minimum 5 years |  |  |  |  |
|  | Documentation | data sheet, manufacturer certificates, connection diagram, installation, operation and maintenance instructions |  |  |  |  |
| 2 | Mandatory components of the supply |  |  |  |  |  |
|  | The system will include: | • LFP battery modules • BMS system • cabinet or rack • cooling/thermal management system • DC protections • cables and connectors • communication modules and cables • all elements necessary for connection to the inverter • mounting and connection • BMS and inverter parameterization • testing of operation in charging and discharging mode • commissioning • training of the beneficiary's personnel • technical documentation and certificates of conformity |  |  |  |  |
| 3 | Special integration requirement |  |  |  |  |  |
|  | The bidder will present, together with the technical offer, the proposed scheme for connecting the storage system to the hybrid inverter, the voltage range of the battery, the maximum charging and discharging current, the BMS communication protocol and the document confirming the compatibility of the equipment. |  |  |  |  |  |