## Arhitectural solutions
No. | Type of equipment requested by BoQ and its data | Bidder’s response
|  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  | Yes, we comply | No, we do not comply (indicate discrepancies)
ITB26/03132: Capital repair and modernization of the “Mihai Eminecu” Gymnasium from Cantemir town
1 | Suspended ceilings made of prefabricated panels including grid system with physical and visual characteristics type Rockfon Artic E24 with partially visible structure and dimensions 600 x 600 x 15mm, class 1/C/0N according to EN 13964
Fire-rated aluminium doors – EI 30 Fire-rated aluminium framed doors, EI 30, complete with thermally insulated aluminium profiles and fire-resistant glazing/panel, providing 30 minutes of fire integrity (E) and thermal insulation (I) in accordance with the applicable fire-resistance standards. Fire resistance classification: EI 30 Integrity: 30 minutes Thermal insulation: 30 minutes Smoke control: Sa/S200. The doors shall be supplied and installed in accordance with the manufacturer's tested system and the relevant applicable standards, including EN 16034 and EN 1634-1, as applicable. Duble leaf doors UI4 (EI30) - 2 pisces and U4 (EI30) -2 pisces.
2 | Plastic floors mounted on the existing substrate, cleaned, including PVC sills, with PVC carpet glued with pre-bonded / Omogenius PVC carpet, thickness = 3 mm; change:PVC profile, PVC sill in PVC PVC connection profile R=30 mm - 0,6 m/m2. Color according to the design.
3 | Epoxy flooring system with a total thickness of 2.0 mm, with anti-slip effect, applied on an existing substrate. The flooring shall be of self-leveling or multilayer epoxy type, applied on a properly prepared concrete substrate.The flooring shall have a total thickness of 2.0 mm (±10%), with anti-slip classification in the range of R10–R12. Mechanical properties shall include compressive strength of at least 70–90 MPa, flexural strength of at least 30 MPa, and adhesion to the substrate of at least 1.5–2.0 MPa (with failure in concrete). The system shall be impermeable to liquids, with negligible water absorption, and resistant to water, cleaning agents, oils, fuels, diluted acids and alkalis, as well as de-icing salts. The flooring shall maintain performance within a service temperature range of approximately -10°C to +60°C. The material shall comply with fire reaction class Bfl-s1 according to EN 13501-1 and meet low VOC emission requirements suitable for indoor environments. Type Full Flake, mix 1 decorative Chips.
4 | Interior partitions made of aluminum profiles with mat sandwich filling composed of PU boards and 1 mm sheet metal on both sides. The windows will be made of 4+4 mm transparent triplex glass. Doors will be equipped with stainless steel door handle set, Hafele Startec model LTD 2170 (or smilar); V1.- V2 1950x2900(h)...2800x2900
5 | WC cubicles, H = 2.0 m, made of aluminum profiles with 12 mm HPL infill (color according to design solutions) and stainless steel support elements, for buildings up to 35 m in height, including fixed panels and door leaves.
6 | Interior wooden doors in a can, with 2 mm metal frame, color RAL 7014 and 44 mm plywood laminated wood plywood canvas, color RAL 1014 with mat varnish. With 1 mm stainless steel protection plate at the bottom and 4+4 mm transparent triplex glass 4+4 mm and stainless steel door handle set, Hafele Startec model LTD 2170 (or smilar); U4- 1150x2100(h)

## Water
No. | Patameter | Specification | Bidder’s response
|  |  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  |  | Yes, we comply | No, we do not comply (indicate discrepancies)
ITB26/03132: Capital repair and modernization of the “Mihai Eminecu” Gymnasium from Cantemir town
1 | Public WC Pan (Side Outlet, Floor-Mounted)
| Product type | Floor-mounted WC pan for public/sanitary facilities
| Outlet type | Horizontal (side/back outlet)
| Installation type | Floor-standing
| Material | Sanitary porcelain / semi-porcelain, glazed finish
| Surface treatment | Smooth, antibacterial glaze, easy to clean
| Flushing system | Washdown or rimless flushing system
| Flush volume | 6/3 L dual flush (or 6 L single flush)
| Cistern type | Close-coupled cistern mounted directly on the bowl
| Cistern material | Ceramic (matching bowl)
| Water inlet | Bottom or side inlet (½")
| Flush mechanism | Mechanical push-button (dual flush recommended)
| Seat and cover | Heavy-duty thermoplastic or duroplast, slow-close (optional)
| Fixing system | Floor fixing bolts with protective caps
| Trap type | P-trap (horizontal outlet)
| Outlet diameter | Ø100 mm
| Dimensions (approx.) | 650–700 mm (L) × 350–380 mm (W) × 750–800 mm (H)
| Water pressure range | 0.5 – 10 bar
| Color | White (standard)
| Compliance | EN 997 / EN 33 (European standards)
| Application | Public buildings, schools, offices, commercial spaces
2 | Public washbasin (lavatory) made of semi-porcelain / sanitary porcelain, mounted on pedestal, with PP siphon
| Product type | Washbasin for public sanitary facilities
| Installation type | Wall-mounted basin with full pedestal
| Material | Sanitary porcelain / semi-porcelain, glazed finish
| Surface treatment | Smooth, hygienic, stain-resistant glaze
| Mounting method | Wall-fixed with anchor bolts; pedestal for aesthetic and pipe concealment
| Pedestal type | Full pedestal (ceramic), matching basin
| Basin dimensions (approx.) | 550–600 mm (W) × 450–500 mm (D)
| Height (installed) | Approx. 800–850 mm from finished floor level
| Tap hole | Single hole Ø35 mm (standard)
| Overflow | Integrated overflow system
| Waste outlet diameter | Ø45 mm
| Siphon | Bottle trap, polypropylene (PP), Ø32 mm
| Water supply connection | ½" flexible connectors
| Fixing kit | Included (bolts, plugs, caps)
| Color | White (standard)
| Water pressure range | 0.5 – 10 bar
| Compliance | EN 14688 (washbasins)
| Application | Public buildings, offices, schools, commercial premises
3 | Wall-Mounted Urinal (Sanitary Porcelain)
| Product type | Urinal for public sanitary facilities
| Installation type | Wall-mounted
| Mounting surface | Reinforced concrete wall
| Material | Sanitary porcelain, fully glazed
| Surface treatment | Smooth, hygienic, stain- and chemical-resistant glaze
| Flushing system | Top or rear inlet (exposed or concealed flush valve)
| Flush control | Manual push valve or automatic sensor (optional)
| Water consumption | 0.5 – 3.0 L per flush (depending on flush valve)
| Water inlet connection | ½"
| Outlet type | Horizontal or vertical outlet
| Waste outlet diameter | Ø50 mm
| Trap type | Integrated trap or external siphon
| Fixing system | Wall anchor bolts with concealed fixings
| Installation height | Rim approx. 600–650 mm above finished floor level
| Dimensions (approx.) | 300–360 mm (W) × 300–350 mm (D) × 500–600 mm (H)
| Color | White (standard)
| Water pressure range | 0.5 – 10 bar
| Compliance | EN 13407 (urinals)
| Application | Public buildings, schools, offices, commercial facilities
4 | Chrome-Plated Mixer Tap with Swivel Spout (Public Toilets)
| Product type | Basin mixer tap for public sanitary facilities
| Installation type | Deck-mounted (single-hole installation)
| Body material | Brass (CuZn), chrome-plated finish
| Surface finish | Polished chrome, corrosion-resistant
| Spout type | Swivel (pivoting) spout
| Spout reach | Approx. 150–200 mm
| Cartridge type | Ceramic cartridge, 35–40 mm
| Control type | Single-lever mixer
| Water supply connection | Flexible hoses ½"
| Aerator | Anti-limescale aerator, M24/M22
| Flow rate | 5–9 L/min (depending on pressure)
| Operating pressure | 1 – 10 bar
| Recommended pressure | 3 bar
| Water temperature range | 5°C – 90°C
| Fixing system | Mounting kit included (gasket, fixing nut, bolts)
| Application | Public toilets, schools, offices, commercial buildings
| Compliance | EN 817 (mechanical mixer taps)
5 | Accessible Wall-Mounted Bath Mixer with Hand Shower
| Product type | Bath mixer tap with hand shower for accessible sanitary rooms
| Installation type | Wall-mounted
| Mounting surface | Brick masonry wall (with concealed pipe connections)
| Body material | Brass (CuZn), chrome-plated
| Surface finish | Polished chrome, corrosion-resistant
| Control type | Single-lever mixer with extended ergonomic handle (accessible use)
| Cartridge type | Ceramic cartridge, 35–40 mm
| Temperature limiter | Adjustable safety stop (anti-scald protection)
| Diverter | Integrated automatic diverter (bath/shower)
| Shower hose | Flexible stainless steel or reinforced PVC, length 1500–2000 mm
| Hand shower | Ergonomic hand shower, anti-limescale nozzles
| Water inlet connection | ½" standard eccentric connections
| Flow rate | 8–12 L/min
| Operating pressure | 1 – 10 bar
| Recommended pressure | 3 bar
| Temperature range | 5°C – 90°C
| Installation height | According to accessibility standards (approx. 900–1100 mm from finished floor)
| Accessibility compliance | EN 12182 / EN 1111 (if thermostatic version)
| Safety features | Anti-scald device, smooth edges, easy-grip lever
| Application | Public buildings, accessible sanitary units, healthcare facilities
| Color | Chrome (standard)

## HAVC
No. | Patameter | Specification | Bidder’s response
|  |  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  |  | Yes, we comply | No, we do not comply (indicate discrepancies)
ITB26/03132: Capital repair and modernization of the “Mihai Eminecu” Gymnasium from Cantemir town
1 | Steel Panel Radiator Type “Korado" 22K 500×1000 or equivalent
| Product type | Steel panel radiator Radik Klasik
| Model | Type 22K (two panels + two convectors)
| Dimensions (H × L) | 500 × 1000 mm
| Depth | Approx. 100 mm
| Material | Cold-rolled steel panels
| Surface finish | Powder-coated, white (RAL 9016 standard)
| Heat output (90/70/20°C) | Approx. 1670 W
| Heat output (75/65/20°C) | Approx. 1400 W
| Maximum operating temperature | 110°C
| Maximum working pressure | 10 bar
| Test pressure | 13 bar
| Water content | Approx. 5–6 liters
| Weight | Approx. 28-30 kg
| Connections | 4 × G 1/2" female threaded (side connections)
| Installation type | Wall-mounted (brackets included)
| Air vent & plug | Included
| Standard compliance | EN 442
2 | Steel panel radiator “Korado" Type 33K 300×1400 or equivalent
| Product type | Steel panel radiator Radik Klasik
| Model | Type 33K (three panels + three convectors)
| Dimensions (H × L × D) | 300 × 1400 × ~155 mm
| Material | Cold-rolled steel panel construction
| Surface finish | Powder-coated white (standard RAL, corrosion-protected)
| Heat output (90/70/20 °C) | ~3238 W
| Heat output (75/65/20 °C) | ~2750 W
| Water content | ~7.42 L
| Weight | ~38.78 kg
| Maximum operating temperature | 110 °C
| Maximum working pressure | 10 bar
| Test pressure | 13 bar
| Connections | 4 × G 1/2″ internal threads
| Connecting pitch | H – 54 mm
| Installation type | Wall-mounted radiator
| Compliance | EN 442 (European radiator standard)
3 | Danfoss Thermostatic Radiator Valve with Pre-Setting RTR-N, DN 15
| Product type | Thermostatic radiator valve with pre-setting
| Model | RTR-N
| Nominal diameter | DN 15 (≈ 1/2″)
| Connection type | Rp 1/2″ internal thread
| Valve configuration | Normal flow type (presetting on the radiator inlet)
| Body material | Brass with corrosion-resistant surface finish
| Presetting | Integrated presetting ring with adjustable Kv steps
| Kv range | Approx. 0.04 – 0.7 m³/h (depending on presetting position)
| Kv at presetting “N” | Approx. 0.73 m³/h
| Max. operating temperature | Up to 120 °C
| Max. working pressure | 10 bar
| Test pressure | 16 bar
| Seal material | EPDM or equivalent elastomer
| Differential pressure tolerance | Up to ~0.6 bar for stable control
| Surface finish | Nickel-plated or chrome plated (depending on manufacturer)
| Standards compliance | EN 215 (Thermostatic radiator valves)
| Accessories | Compatible with thermostatic heads (RA, RAS series or equivalent)
4 | Danfoss Radiator Shut-off Valve (RLV), DN 15
| Product type | Radiator shut-off / lockshield valve
| Model | RLV, DN 15
| Connection size | R 1/2″ (internal thread) – radiator and system connections
| Design | Straight lockshield valve
| Body material | Brass with nickel-plated finish (corrosion-resistant)
| Maximum operating temperature | 120 °C
| Maximum working pressure | 10 bar
| Test pressure | 16 bar
| Kv (flow coefficient) | Approx. 2.20–2.50 m³/h
| Seal material | EPDM or equivalent
| Surface finish | Nickel plated
| Thread standard | ISO 7/1 (R 1/2″)
| Type variants | Straight or angled, standard or self-sealing tailpiece
5 | Thermostatic Element Danfoss RTR 7090
| Model / Part No. | RTR 7090 / 013G7090
| Type | Thermostatic radiator thermostat element
| Application | For automatic temperature control of radiator valves
| Compatibility | Designed for RTR series radiator valves (e.g., RTR-N, RTR-G), can be combined with appropriate radiator valve bodies
| Sensing element | Gas-filled bulb sensor
| Mounting / Connection | Clip-on type (quick clip fitting to valve)
| Adjustment range (room air temperature) | 5 °C to 26 °C
| Temperature range, operational | Min. 5 °C – Max. 26 °C setpoint range
| Colour | White
| Max. permitted system temperature | Approx. 120 °C (typical TRV rating for paired valves)
| Max. working pressure | Approx. 10 bar (based on typical radiator thermostatic valve ratings)
| Ratio / Sensitivity | Proportional direct-acting thermostat with small proportional band
| Housing material | Plastic body with internal sensing element
| Standards compliance | EN 215 (when combined with compliant radiator valve)
| Color | Green / white / grey (manufacturer dependent)
| Marking | Manufacturer, Ø20, PN20, standard EN ISO 15874
| Compatibility | Compatible with PP-R fittings and metal inserts
| Standards compliance | EN 215 (when combined with compliant radiator valve)
6 | Technical Specification Schedule – AHU AR1 Atrea Duplex Multi 10 000 complete with EC fans, plate heat recovery, hot water heating. Minimum acceptable or equivalent
| Equipment | Heat Recovery Ventilation Unit (HRV)
| Model | DUPLEX 10000 Multi or equivalent
| Installation | Indoor
| Supply air flow rate | Up to 11,100 m³/h
| Extract air flow rate | Up to 10,700 m³/h
| Heat recovery type | Counter-flow heat exchanger
| Heat recovery efficiency | Up to 93%
| Fans | EC fans, electronically commutated
| Power supply | 400 V / 3 Ph / 50 Hz
| Maximum electrical power | Approx. 10.7 kW
| External static pressure | 200 Pa reference point
| Heating capacity | Up to 95 kW, water heating coil
| Cooling capacity | Up to 65 kW, chilled-water coil
| Bypass | Integrated / automatic bypass
| Filters | Supply and extract air filters, according to design
| Condensate drain | Ø32 mm
| Maximum dimensions (H × W × L) | Approx. 1,795 × 1,620 × 3,370 mm
| Air connection | Approx. 900 × 710 mm
| Noise level | Approx. 53 dB(A) at 3 m, reference operating point
| Controls | Integrated automatic control system
| Control functions | Airflow control, temperature control, heat recovery and bypass control
| Operating modes | Automatic / manual / scheduled operation
| Casing | Thermally insulated, corrosion-resistant construction
| Heat exchanger | High-efficiency, counter-flow type
| Energy efficiency | In accordance with applicable ErP requirements
| Commissioning | Testing, adjustment and commissioning included
| Documentation | Technical documentation, operation and maintenance manuals
| Warranty | Minimum as specified in the tender documents
7 | Technical Specification Schedule – AHU AR12 Atrea Duplex Multi 3500 complete with EC fans, plate heat recovery, hot water heating. Minimum acceptable or equivalent
| System type | Mechanical ventilation unit with heat recovery (HRV)
| Model / Series | Duplex 3500 Multi-V
| Airflow | 2,195 m³/h
| Static pressure | 450 Pa
| Fan power | 2.50 kW
| Fan speed | 2,970 rpm
| Current draw | 3.8 A
| Supply voltage | 400 V, 3-phase
| Airflow | 2,195 m³/h
| Static pressure | 450 Pa
| Fan power | 2.50 kW
| Fan speed | 2,970 rpm
| Current draw | 3.8 A
| Supply voltage | 400 V, 3-phase
| Heat recovery core | Counterflow / plate or rotary wheel (high efficiency)
| Heat recovery efficiency | Typically 60–85 % (application-dependent)
| Control system | Integrated control panel with speed stages
| Filters | Supply and extract filters (e.g., G4/F7 or equivalent)
| Housing | Galvanized steel with internal thermal/acoustic insulation
| Duct connection | Circular/rectangular spigots to match duct system
| Bypass | Optional automatic summer bypass
| Noise level | Dependent on airflow and installation design
| Protection class | Usually IP rating suitable for mechanical rooms
| Application | Ventilation with energy recovery in commercial/public spaces
| Standards / Compliance | CE marked; compliant with EN ventilation standards
8 | Duct Fan VENTS VKMS 160 or equivalent
| Model | VKMS 160
| Equipment type | Centrifugal duct fan
| Application | Supply and exhaust ventilation systems
| Duct connection diameter | 160 mm
| Casing material | Galvanized steel
| Motor type | Asynchronous motor with external rotor
| Power supply | 230 V / 50 Hz
| Motor power | 85 W
| Rated current | 0.40 A
| Maximum air flow | Up to approx. 460 m³/h
| Maximum static pressure | Up to approx. 300 Pa
| Motor speed | Approx. 2,600 rpm
| Motor protection | IP54
| Thermal protection | Integrated automatic thermal protection
| Operating air temperature | -25°C to +60°C
| Installation position | Any position
| Speed control | Compatible with speed controller
| Casing | Galvanized steel
| Electrical connection | Terminal box
| Mounting | Directly into round ventilation duct
| Noise level | According to manufacturer's technical data

## Electrical
No. | Patameter | Specification | Bidder’s response
|  |  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  |  | Yes, we comply | No, we do not comply (indicate discrepancies)
ITB26/03132: Capital repair and modernization of the “Mihai Eminecu” Gymnasium from Cantemir town
1 | Recessed LED Panel, 600×600 mm, 35 W, 4000 K
| Product type | Recessed LED ceiling luminaire (LED panel)
| Model / Format | 600 × 600 mm (suitable for 600×600 mm ceiling grid)
| Rated power | 35 W
| Light source | Integrated LED modules
| Color temperature | 4000 K (neutral white)
| Rated luminous flux | ≈ 3000–3500 lm (typical from a 35 W panel)
| Efficacy | ≈ 85–100 lm/W (dependent on manufacturer)
| CRI (Color Rendering Index) | ≥ 80 (≥ Ra80)
| Beam angle | ≈ 120° (wide uniform distribution)
| Driver type | External / integrated LED driver (electronic)
| Input voltage | 220–240 V AC, 50/60 Hz
| Power factor | ≥ 0.90
| Dimmable | Optional (DALI / 1–10 V / phase-cut, manufacturer dependent)
| Housing material | Aluminium frame + steel back housing
| Diffuser / Optics | Opal / microprismatic diffuser for uniform glare-free light
| Mounting type | Recessed into suspended ceiling grid (T-bar)
| Protection class | IP20 (indoor use)
| IK rating | IK04–IK05 (impact resistance)
| Operating temperature | 0 °C to +40 °C
| Lifetime | ≥ 50,000 h (L80 B10)
| Certifications | CE
| Finish / Color | White frame (powder coated)
2 | Linear LED Light, 1200 mm, 45 W, 4000 K
| Product type | Linear LED luminaire
| Length | 1200 mm
| Rated power | 45 W
| Light source | Integrated LED
| Color temperature | 4000 K (neutral white)
| Luminous flux | ≈ 3900–4500 lm (typical from a 45 W LED)
| Efficacy | ≈ 85–100 lm/W (dependent on model)
| Color rendering (CRI) | ≥ 80 (≥ Ra80)
| Beam angle | 120° (wide light distribution)
| Driver type | Built-in / external electronic LED driver
| Input voltage | 220–240 V AC, 50/60 Hz
| Power factor | ≥ 0.90
| Dimmable | Optional (DALI / 1–10 V / phase-cut – model dependent)
| Housing material | Aluminium body with steel end caps
| Diffuser | Opal or prismatic polycarbonate for uniform light
| Protection class | IP20 (indoor use)
| IK rating | IK04–IK05 (impact resistant)
| Operating ambient temp | 0 °C to +40 °C
| Lifetime | ≥ 50,000 h (L80)
| Finish / Color | White (standard)
| Certifications | CE, RoHS, EMC
| Application | Offices, corridors, retail, education, industrial interiors
3 | Illuminated Direction Indicator with Battery
| Product type | Illuminated directional indicator / emergency exit arrow sign
| Rated LED power | 3 W
| Light source | High-efficiency LEDs
| Illumination color | Green (standard for emergency direction signs)
| Symbol / Arrow type | Directional arrow or pictogram (configurable: left / right / up / down)
| Supply voltage | 220–240 V AC, 50 Hz (primary mains)
| Backup power | Rechargeable battery (internal)
| Battery type | Sealed lead-acid (SLA) or NiMH (model dependent)
| Battery autonomy | ≥ 3 hours (in emergency mode)
| Charge time | ≤ 24 hours to full charge
| LED lifetime | ≥ 50,000 h
| Viewing distance | ≥ 20–25 m (depending on size and installation)
| Ingress protection | IP20 (indoor), optional higher rating on request
| Mounting | Wall or ceiling (surface mounted)
| Housing material | ABS / polycarbonate flame-retardant enclosure
| Operating temperature | 0 °C to +40 °C (typical)
| Emergency testing | Built-in test button (optional)
| Standards / Compliance | Compliant with EN 50172 / EN 1838 (emergency lighting)
| Indicators | Charge / test LED indicators
| Finish / Color | White housing (standard)
4 | Distribution Board, 36 Modules (Flush-Mounted)
| Product type | Electrical distribution board (consumer unit)
| Model / Type | Flush-mounted distribution board, 36 modules (ЩРв-36 or equivalent)
| Installation type | Recessed / flush-mounted (in-wall installation)
| Number of modules | 36 DIN modules (3 rows × 12 modules typical)
| Rated voltage | 230/400 V AC, 50 Hz
| Rated current | Up to 63–100 A (depending on manufacturer)
| Protection class | IP30–IP40 (indoor use)
| Impact resistance | IK07 (typical)
| Material | Metal enclosure with powder coating or high-quality ABS (model dependent)
| Door type | Solid or transparent hinged door
| Mounting rail | Standard 35 mm DIN rail
| Neutral busbar (N) | Included
| Protective earth busbar (PE) | Included
| Terminal type | Screw terminals
| Cable entry | Top and bottom knockouts
| Operating temperature | –5 °C to +40 °C
| Color | White (RAL 9016 typical)
| Standards / Compliance | IEC 61439-1 / IEC 61439-3, CE
5 | Residual Current Circuit Breaker with Overcurrent Protection (RCBO), 2P, C16A, 10 mA, 6 kA
| Product type | RCBO (Residual Current Circuit Breaker with Overcurrent protection)
| Number of poles | 2P (Phase + Neutral)
| Rated current (In) | 16 A
| Tripping characteristic | Type C (magnetic curve C)
| Rated residual current (IΔn) | 10 mA
| Breaking capacity | 6 kA
| Rated voltage (Ue) | 230 V AC
| Frequency | 50/60 Hz
| Residual current type | Type AC or Type A (model dependent)
| Mounting | 35 mm DIN rail
| Protection degree | IP20 (installed in enclosure)
| Mechanical endurance | ≥ 10,000 operations
| Electrical endurance | ≥ 4,000 operations
| Terminal type | Screw clamp terminals
| Standards | IEC 61009-1
6 | Uninterruptible Power Supply (UPS), 4 kVA
| Product type | Uninterruptible Power Supply (UPS)
| Rated power capacity | 4 kVA
| Active power (typical) | 3.2–3.6 kW (depending on power factor 0.8–0.9)
| UPS topology | Online double-conversion / Line-interactive (model dependent)
| Input voltage | 220–240 V AC
| Input frequency | 50/60 Hz (auto sensing)
| Output voltage | 230 V AC ±1–2%
| Output frequency | 50/60 Hz ±0.1 Hz (online type)
| Waveform | Pure sine wave
| Transfer time | 0 ms (online) / 2–10 ms (line-interactive)
| Battery type | Sealed lead-acid (VRLA) or external battery pack
| Battery autonomy | 5–15 minutes at full load (extendable with external batteries)
| Recharge time | 4–8 hours to 90% capacity
| Bypass | Automatic and manual bypass (model dependent)
| Efficiency | ≥ 90% (online), ≥ 95% (eco mode)
| Protection features | Overload, short-circuit, battery deep discharge, overtemperature
| Communication ports | USB / RS-232 / SNMP (optional network card)
| Display | LCD display with load and battery status
| Cooling | Forced air cooling (internal fans)
| Installation type | Tower or Rack-mount (model dependent)
| Protection class | IP20 (indoor use)
| Operating temperature | 0 °C to +40 °C
| Standards / Compliance | IEC 62040-1, IEC 62040-2, CE

## Low voltage
No. | Patameter | Specification | Bidder’s response
|  |  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  |  | Yes, we comply | No, we do not comply (indicate discrepancies)
ITB26/03132: Capital repair and modernization of the “Mihai Eminecu” Gymnasium from Cantemir town
1 | Network Video Recorder DS-8632NXI-I8/S MP/32-ch@1080p, 2 HDMI, 2 VGA, 8K or dual 4K video outputs,
| Product | 32-channel AcuSense Network Video Recorder (NVR) DS-8632NXI-I8/S
| Type | Professional IP NVR (2U chassis)
| Video inputs | Up to 32 IP cameras
| Max recording resolution | Up to 32 MP (IP cameras)
| Video compression | H.265+/H.265/H.264+/H.264
| Incoming bandwidth | Up to 320 Mbps
| Outgoing bandwidth | Up to 256 Mbps
| Decoding capability | Up to 32-ch @1080p
| HDMI output | Up to 4K (3840×2160)
| VGA output | Up to 1920×1080
| Audio | 2-ch audio out, 1-ch two-way audio
| AI analytics | AcuSense (deep learning: human/vehicle detection)
| Facial recognition | Up to 4-ch video / 8-ch image
| Perimeter protection | Up to 4 channels
| ANPR support | Yes (via cameras)
| Storage | 8 × SATA HDD bays
| Max HDD capacity | Up to 16 TB per disk
| RAID support | RAID 0/1/5/6/10
| eSATA | 1 port
| USB ports | 2 × USB 2.0 (front), 2 × USB 3.0 (rear)
| Network interface | 1 × RJ-45 Gigabit Ethernet
| Remote users | Up to 128 connections
| Protocols | TCP/IP, ONVIF, RTSP, HTTPS, etc.
| Alarm I/O | 16 in / 9 out
| Power supply | 100–240 VAC, 50/60 Hz
| Power consumption | ≤30 W (without HDD)
| Operating temperature | -10°C to +55°C
| Dimensions | 440 × 457 × 94 mm
| Weight | ≤7.1 kg (without HDD)
| Certifications | CE, CB, WEEE, UKCA
2 | Hikvision DS‑2CD1067G2‑LUF (a 6 MP outdoor/indoor fixed network camera with built-in mic and audio support
| Product type | Fixed network (IP) dome camera
| Image sensor | 1/2.7″ Progressive CMOS
| Resolution | 6 MP (3072 × 2048)
| Lens | Fixed 2.8 mm (wide) / optional 4 mm variants
| Field of View (approx.) | 102° (H) × 55° (V) × 124° (D)
| Min. Illumination | 0.01 lux @ (F1.2, AGC ON)
| Day/Night | IR cut filter with auto switch
| IR Range | Up to 10–15 m (model dependent)
| Video Compression | H.265 / H.264 / MJPEG
| Max. Frame Rate | 6 MP @ 20 fps
| Video Streaming | 3 concurrent streams
| WDR | Digital WDR (Wide Dynamic Range)
| BLC / HLC | Yes (Backlight / Highlight compensation)
| Noise Reduction | 3D Digital Noise Reduction (3D DNR)
| Audio | Built-in microphone
| Network | 1 × RJ45 10/100 Mbps
| PoE | 802.3af PoE (power over Ethernet)
| Storage | MicroSD/SDHC/SDXC card slot (up to 256 GB)
| Smart features | Motion detection, region of interest, privacy mask
| ONVIF | Profiles S/G compatible
| Power | PoE or 12 V DC
| Operating Temp. | –30 °C to +60 °C
| Ingress Protection | IP67 (dust & water resistant)
| IK Rating | IK10 (impact resistant)
| Housing material | Metal / plastic weatherproof casing
| Dimensions | Approx. Ø109 × 78 mm
| Weight | ~0.4 kg
3 | Hikvision DS-2CD1147G2H-LIU(F), a 4 MP network camera with built-in IR and advanced features
| Product type | Network (IP) turret camera
| Image sensor | 1/3″ Progressive Scan CMOS
| Effective pixels | 4 MP (2688 × 1520)
| Lens | 2.8 mm fixed lens (horizontal FOV ~102°)
| Maximum resolution | 2688 × 1520
| Min. illumination | 0.005 lux @ (F1.6, AGC ON)
| Day/Night | True D/N with mechanical IR cut filter
| IR illumination | Up to 30 m range (built-in IR LEDs)
| Video compression | H.265 / H.264 / MJPEG
| Max. frame rate | 4 MP @ 30 fps
| Video streams | 3 independent streams
| Wide Dynamic Range | Digital WDR (120 dB)
| Noise reduction | 3D DNR (Digital Noise Reduction)
| ROI / BLC / HLC | Yes (Region of Interest / Backlight / Highlight Comp)
| Audio | Built-in microphone
| Smart features | Motion detection, line crossing, intrusion detection (model dependent)
| Network | 1 × RJ45 10/100 Mbps
| Power | PoE (802.3af) or 12 V DC
| Power consumption | < 6 W typically
| On-board storage | MicroSD/SDHC/SDXC up to 256 GB
| Operating temp. | –30 °C to +60 °C
| Ingress protection | IP67 weatherproof
| Impact protection | IK10 vandal resistant
| Housing material | Metal base with plastic/metal dome
| Dimensions | Approx. Ø110 × 93 mm
| Weight | ~0.5 kg
4 | Fiber Optic Patch Panel FOBX24-1U-8LCUD03
| Product | Fiber optic patch panel FOBX24-1U-8LCUD03 (or equivalent)
| Type | Rack-mounted fiber optic distribution panel
| Form factor | 19” rack, 1U height
| Application | Fiber optic signal distribution and termination in telecom and LAN systems
| Fiber type | Multimode OM3 (50/125 µm)
| Connector type | LC Duplex
| Number of adapters | 8 × LC duplex (installed)
| Max capacity | Up to 24 LC ports (modular panel)
| Included components | LC pigtails, splice tray, heat shrink sleeves (KDSZ)
| Splice tray | 1 cassette (capacity up to 32 splices)
| Mounting type | Rack-mounted (fixed)
| Material | Metal корпус (steel), powder-coated
| Color | Grey (RAL 7035)
| Protection rating | IP22
| Impact resistance | IK07
| Dimensions (W×D×H) | 405 × 212 × 40 mm
| Weight | ~2.5–2.7 kg
| Cable management | Internal fiber routing and фиксация кабеля
| Installation accessories | Mounting brackets, screws, cable ties included
| Operating environment | Indoor installation
| Function | Splicing, termination, and patching of fiber optic cables
5 | Cloud Core Router CCR1016-12S-1S+
| Product | Cloud Core Router CCR1016-12S-1S+
| Type | Carrier-grade router / 1U rackmount
| Architecture | TILE
| CPU | Tilera TLR4-01680
| CPU cores | 16 cores
| CPU frequency | 1.2 GHz
| RAM | 2 GB
| Storage | 128 MB NAND
| Operating system | RouterOS (Level 6 license)
| Throughput | Up to ~20 Gbps (fast path)
| Ethernet / Fiber ports | 12 × SFP (1G), 1 × SFP+ (10G)
| Additional ports | 1 × USB, 1 × RJ45 serial console
| Memory expansion | microSD slot
| Display | Integrated LCD touchscreen
| Power supply | Dual redundant AC (100–240 V)
| Power consumption | Up to ~47.5 W
| Cooling | Active cooling (2 fans)
| Dimensions | 443 × 197 × 44 mm (1U rack)
| Operating temperature | -20°C to +60°C
| Protection rating | IP20
| MTBF | ~200,000 hours
| Certifications | CE, EAC, RoHS
| Included accessories | Rack ears, power cables, RJ45 SFP module
6 | Industrial PoE Switch TSX-U-2GX/SFP-24GTP-R or equivalent
| Manufacturer | EKF
| Type | Layer 2 unmanaged Ethernet switch
| Application | Industrial networks, CCTV, structured cabling
| Total ports | 26 ports
| RJ45 ports | 24 × 10/100/1000Base-T (Gigabit Ethernet)
| PoE support | Yes, 24 ports with PoE (up to 30 W per port)
| Uplink ports | 2 × SFP (1 Gbps)
| Switching capacity | ~52 Gbps
| MAC address table | Auto-learning, auto-aging
| Management | Unmanaged (plug & play)
| Installation | 19” rack mounting (1U)
| Power supply | 100–240 VAC
| Power per PoE port | Up to 30 W
| Housing material | Metal (industrial grade)
| Dimensions | ~440 × 280 × 44 mm
| Operating temperature | Approx. -10°C to +50°C
| Cooling | Passive / active (depending on version)
| Protection | Industrial design for stable operation
| Function | Data switching + PoE power supply
| Use cases | IP cameras, access points, VoIP, industrial LAN
7 | SFP Optical Transceiver TSX-SFP-HS2D-13-20 or equivalent
| Product | SFP optical transceiver TSX-SFP-HS2D-13-20 (or equivalent)
| Type | SFP (Small Form-factor Pluggable) optical module
| Application | Fiber optic data transmission (LAN, telecom, CCTV networks)
| Data rate | 2.5 Gbps
| Standards | STM-8 / OC-24 / Gigabit Ethernet
| Fiber type | Single-mode (SM)
| Transmission distance | Up to 20 km
| Wavelength | 1310 nm
| Connector type | Duplex (2 fibers)
| Form factor | SFP hot-pluggable module
| Power supply | 3.3 V
| Housing material | Metal корпус
| Mounting | Plug-in (latch mechanism)
| Dimensions | ~9 × 14 × 56 mm
| Weight | ~0.03 kg
| Series | PROxima
| Function | Optical signal transmission and reception
8 | EKF SW900PRO-EBBRT-78 Battery Pack or equivalent
| Product | External battery pack SW900PRO-EBBRT-78 (or equivalent)
| Type | External battery module for UPS
| Application | Extending backup time of UPS systems
| Compatible UPS | E-Power SW900Pro-RT / RTB (3000 VA class)
| Battery type | Sealed lead-acid (VRLA)
| Number of batteries | 8 pcs
| Battery capacity | 7 Ah each
| Battery voltage | 12 V per battery
| Total system voltage | 96 V DC
| Mounting | Rackmount / standalone (1U/2U form factor)
| Dimensions (W×D×H) | ~440 × 465 × 88 mm
| Weight | ~15–21.8 kg (depending on config)
| Housing | Metal корпус
| Cooling | Passive
| Protection rating | IP20
| Function | Provides extended autonomy time for UPS
| Series | E-Power SW900Pro
9 | Wireless Access Point RBwAPG-5HacT2HnD
| Type | Dual-band wireless access point (outdoor/indoor)
| Wi-Fi standards | 802.11a/b/g/n/ac
| Frequency bands | 2.4 GHz and 5 GHz (simultaneous)
| Max data rate | Up to 300 Mbps (2.4 GHz) + 1300 Mbps (5 GHz)
| Wi-Fi class | AC1600
| Antennas | Integrated omni-directional
| Antenna gain | ~2 dBi
| MIMO | 2×2 (2.4 GHz), 3×3 (5 GHz)
| Ethernet ports | 1 × 10/100/1000 Mbps (Gigabit)
| CPU | QCA9556, 720 MHz
| CPU cores | 1
| RAM | 64 MB
| Storage | 16 MB Flash
| Operating system | RouterOS (Level 4 license)
| Power supply | PoE-in (802.3af/at), 11–57 V
| Max power consumption | ~12 W
| Protection rating | IP54 (weatherproof)
| Operating temperature | -40°C to +70°C
| Mounting | Wall, ceiling, or pole mounting
| Cooling | Passive
| Dimensions | 185 × 85 × 30 mm
| MTBF | ~100,000 hours
| Certifications | CE, FCC, EAC, RoHS
10 | Previdia UltraVox 2/16 CAN, TCP/IP or equivalent
| Type | Addressable fire detection + EVAC (voice alarm) control panel
| Configuration | 2 loops standard, expandable up to 16 loops
| System architecture | Modular (IFM / IFAM modules on CAN BUS)
| Communication bus | CAN BUS (internal modules)
| Network connectivity | TCP/IP Ethernet + RS485 (Hornet+) + IDANet
| BMS integration | Modbus TCP/IP, BACnet support
| Networking capacity | Up to 48 panels in one system
| Power supply | 90–264 VAC, 50/60 Hz
| Output voltage | ~26–27.6 V DC
| Power capacity | 1000 W per PSU (expandable up to 4000 W)
| Battery backup | 2 × 12 V (17–38 Ah typical)
| Loop type | Addressable loops (detectors, modules)
| Max modules | Up to 32 internal modules per system
| Voice evacuation | Integrated EVAC system (EN54-16 compliant)
| Audio system | 100 V speaker lines with supervision
| Amplifiers | 250 W modular amplifiers
| Control interface | Touch display (front panel)
| Protocols | TCP/IP, Modbus, proprietary INIM
| Cloud connectivity | INIM Cloud (remote monitoring)
| Protection rating | IP30
| Operating temperature | -5°C to +40°C
| Installation | Wall-mounted cabinet (expandable multi-cabinet system)
| Functions | Fire detection, alarm, evacuation, PA, system monitoring
11 | FPMCPU front CPU module (or equivalent)
| Product | FPMCPU front CPU module (or equivalent)
| Type | Main control unit (front panel CPU module)
| Application | Previdia Ultra / UltraVox / Previdia Max fire alarm systems
| Function | Central control and coordination of all system modules
| Installation | Mounted on front panel of control cabinet
| System connection | CAN drive bus (internal communication)
| Display | Graphic color touchscreen (~7”)
| Control interface | Touch + buttons + LED indicators
| CPU architecture | Dual CPU (main + backup)
| Redundancy | Built-in backup CPU ensures basic operation in case of failure
| Role modes | Main unit / backup unit / remote repeater
| Ethernet | Yes (TCP/IP for networking & remote control)
| RS485 interfaces | 2 channels: repeater + BMS (Modbus RTU)
| USB port | Mini-USB for configuration
| Serial port | RS232 for programming
| microSD slot | Yes (data storage / configuration)
| Power supply | ~27.6 V DC (from PSU module)
| Power consumption | ~130–140 mA typical
| Operating temperature | -5°C to +40°C
| Number per panel | Up to 2 (main + backup)
| Repeater capacity | Up to 14 units as remote keyboards
| Housing | Plastic front module (light or dark grey)
| Series | FPM (Front Panel Modules)
12 | Ceiling loudspeaker SPI-C66100 (or equivalent)
| Product | Ceiling loudspeaker SPI-C66100 (or equivalent)
| Type | Ceiling-mounted loudspeaker for voice evacuation (EVAC)
| Application | Fire alarm / voice evacuation / PA systems
| Certification | EN54-24 compliant (fire safety standard)
| Speaker size | 6.5”
| Rated power | 6 W
| Power settings | 1.5 / 3 / 6 W (selectable)
| Operating voltage | 70 V / 100 V line
| Sound pressure level (SPL) | ~95 dB (1W @ 1 m)
| Frequency response | 130 Hz – 15 kHz
| Transformer | Built-in line transformer
| Mounting type | Flush ceiling mounting
| Fixing method | Spring clips (quick installation)
| Housing | Metal корпус with rear protection dome
| Front grille | Metal
| Terminals | Ceramic terminal block
| Protection | Thermal fuse (overload protection)
| IP rating | IP21
| Dimensions | ~200 × 100 mm
| Cut-out diameter | ~175 mm
| Weight | ~0.9 kg
| Color | White
| Installation environment | Indoor (Type A)
13 | Addressable optical smoke detector ES0020RE (or equivalent)
| Product | Addressable optical smoke detector ES0020RE (or equivalent)
| Type | Addressable photoelectric (optical) smoke detector
| Application | Fire detection in buildings (offices, public, residential)
| Detection principle | Optical (light scattering)
| System compatibility | INIM addressable fire alarm systems (Previdia / SmartLoop)
| Communication | Addressable loop communication
| Operating voltage | From loop (approx. 15–30 V DC)
| Current consumption | Low (typical for addressable detectors)
| LED indication | 360° dual LED (alarm indication)
| Remote indicator | Supported (remote LED output)
| Sensitivity | EN54 compliant, adaptive compensation for dust
| Isolation | Built-in short-circuit isolator
| Addressing | Automatic / software addressing
| Base compatibility | Compatible with standard INIM detector bases
| Operating temperature | -5°C to +40°C
| Humidity | Up to 95% RH (non-condensing)
| Protection rating | IP40 (with base)
| Material | Flame-retardant plastic
| Color | White
| Diameter | ~100 mm
| Height | ~50 mm (with base)
| Weight | ~100 g
| Certification | EN54-7 compliant (smoke detector standard)

## Elevator_Amendment 1
No. | Patameter | Specification | Bidder’s response
|  |  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  |  | Yes, we comply | No, we do not comply (indicate discrepancies)
ITB26/03132: Capital repair and modernization of the “Mihai Eminecu” Gymnasium from Cantemir town Amendment no. 1
1 | Elevator NIKAN 5000 MRL or equivalent
| Model | 5000 MRL (Machine Room-Less)
| Type | Electric traction elevator
| Rated load | 630 kg
| Passenger capacity | 2 persons
| Number of stops | 3
| Rated speed | 1.0 m/s
| Drive system | Gearless traction machine
| Machine room | Without (MRL configuration)
| Control system | Microprocessor-based collective control
| Power supply | 380–400V, 3-phase, 50 Hz
| Door type | Automatic sliding doors (center opening)
| Door opening width | Minim 900 mm (standard for 630 kg) with access for persons with disabilities
| Cabin internal dimensions | Minim 1100 × 1400 mm (W × D)
| Shaft dimensions (min.) | Approx. 1600 × 1600 mm (acording drawings)
| Pit depth | Approx. 1200 mm (typical)
| Overhead height | Approx. 3600 mm (typical)
| Safety system | Overspeed governor, safety gear, door interlocks
| Drive control | VVVF (Variable Voltage Variable Frequency)
| Noise level | Low-noise operation
| Compliance | EN 81-20 / EN 81-50 (or local equivalent)
| Interior finish | Stainless steel (as per design)
| Lighting | LED ceiling lighting
| Emergency system | Emergency lighting & alarm
| Optional features | ARD (Automatic Rescue Device), GSM module, access control