Annex 4

Technical Compliance Table

| Item | Minimum Specifications |  | Compliance Yes/No (provide details) |
| --- | --- | --- | --- |
|  | Air Conditioners |  |  |
| 1 | Type 1 | Split air conditioning system, wall mounted, inverter |  |
|  | Reverse Cycle System (Cooling & Heating) | Yes |  |
|  | Other features | Moisture removal, ventilation, auto |  |
|  | Cooling/Heating Capacity (BTU/h) | 24,000 BTU/24,000 BTU (circa 40 m2 of office space) |  |
|  | Permissible Range of Outdoor Temp, ºC | Cooling: -10/+40; Heating: -10/+20 |  |
|  | Indoor/Outdoor Sound Level, dB | Max 35/60 |  |
|  | Seasonal Energy Efficiency Ratio (SEER)/ Seasonal Coefficient of Performance (SCOP) | Min 6.1/Min 4.6 |  |
|  | Energy saving Rank (Cooling/Heating) | Min A++/A++ |  |
|  | Refrigerant | R410A |  |
|  | Input Power (Indoor Unit/Outdoor Unit) | 1F, 220 - 240 V, 50 Hz |  |
|  | Standard mounting and adjustment services (including consumables and additional services, like supports, pipes, ducts, cable, etc.) | Yes |  |
| 2 | Type 2 | Split air conditioning system, wall mounted, inverter |  |
|  | Reverse Cycle System (Cooling & Heating) | Yes |  |
|  | Other features | Moisture removal, ventilation, auto |  |
|  | Cooling/Heating Capacity (BTU/h) | 18,000 BTU/18,000 BTU (30-40 m2 of office space) |  |
|  | Permissible Range of Outdoor Temp, ºC | Cooling: -10/+40; Heating: -10/+20 |  |
|  | Indoor/Outdoor Sound Level, dB | Max 35/60 |  |
|  | Seasonal Energy Efficiency Ratio (SEER)/ Seasonal Coefficient of Performance (SCOP) | Min 6.1/Min 4.6 |  |
|  | Energy saving Rank (Cooling/Heating) | Min A++/A++ |  |
|  | Refrigerant | R410A |  |
|  | Input Power | 1F, 220 - 240 V, 50 Hz |  |
|  | Standard mounting and adjustment services (including consumables and additional services, like supports, pipes, ducts, cable, etc.) | Yes |  |
| 3 | Type 3 | Split air conditioning system, wall mounted, inverter |  |
|  | Reverse Cycle System (Cooling & Heating) | Yes |  |
|  | Other features | Moisture removal, ventilation, auto |  |
|  | Cooling/Heating Capacity (BTU/h) | 12,000 BTU/12,000 BTU (20-30 m2 of office space) |  |
|  | Permissible Range of Outdoor Temp, ºC | Cooling: -10/+40; Heating: -10/+20 |  |
|  | Indoor/Outdoor Sound Level, dB | Max 35/60 |  |
|  | Seasonal Energy Efficiency Ratio (SEER)/ Seasonal Coefficient of Performance (SCOP) | Min 6.1/Min 4.6 |  |
|  | Energy saving Rank (Cooling/Heating) | Min A++/A++ |  |
|  | Refrigerant | R410A |  |
|  | Input Power | 1F, 220 - 240 V, 50 Hz |  |
|  | Standard mounting and adjustment services (including consumables and additional services, like supports, pipes, ducts, cable, etc.) | Yes |  |
| 4 | Type 4 | Split air conditioning system, wall mounted, inverter |  |
|  | Reverse Cycle System (Cooling & Heating) | Yes |  |
|  | Other features | Moisture removal, ventilation, auto |  |
|  | Cooling/Heating Capacity (BTU/h) | 9,000 BTU/9,000 BTU (10-20 m2 of office space) |  |
|  | Permissible Range of Outdoor Temp, ºC | Cooling: -10/+40; Heating: -10/+20 |  |
|  | Indoor/Outdoor Sound Level, dB | Max 35/60 |  |
|  | Seasonal Energy Efficiency Ratio (SEER)/ Seasonal Coefficient of Performance (SCOP) | Min 6.1/Min 4.6 |  |
|  | Energy saving Rank (Cooling/Heating) | Min A++/A++ |  |
|  | Refrigerant | R410A |  |
|  | Input Power | 1F, 220 - 240 V, 50 Hz |  |
|  | Standard mounting and adjustment services (including consumables and additional services, like supports, pipes, ducts, cable, etc.) | Yes |  |