**Annex 4**

**Technical Compliance Table**

|  |  |  |
| --- | --- | --- |
| **Item** | **Minimum Specifications** | **Compliance****Yes/No***(provide details)* |
| **Air Conditioners** |
| 1 | **Type 1** | Split air conditioning system, wall mounted, inverter |  |
| Reverse Cycle System (Cooling & Heating) | Yes |  |
| Other features  | Moisture removal, ventilation, auto |  |
| Cooling/Heating Capacity (BTU/h) | 24,000 BTU/24,000 BTU (circa 40 m2 of office space) |  |
| Permissible Range of Outdoor Temp, ºC | Cooling: -10/+40; Heating: -10/+20 |  |
| Indoor/Outdoor Sound Level, dB | Max 35/60 |  |
| Seasonal Energy Efficiency Ratio (SEER)/ Seasonal Coefficient of Performance (SCOP) | Min 6.1/Min 4.6 |  |
| Energy saving Rank (Cooling/Heating) | Min A++/A++ |  |
| Refrigerant  | R410A |  |
| Input Power (Indoor Unit/Outdoor Unit) | 1F, 220 - 240 V, 50 Hz |  |
| Standard mounting and adjustment services (including consumables and additional services, like supports, pipes, ducts, cable, etc.) | Yes |  |
| 2 | **Type 2** | Split air conditioning system, wall mounted, inverter  |  |
| Reverse Cycle System (Cooling & Heating) | Yes |  |
| Other features  | Moisture removal, ventilation, auto |  |
| Cooling/Heating Capacity (BTU/h) | 18,000 BTU/18,000 BTU (30-40 m2 of office space) |  |
| Permissible Range of Outdoor Temp, ºC | Cooling: -10/+40; Heating: -10/+20 |  |
| Indoor/Outdoor Sound Level, dB | Max 35/60 |  |
| Seasonal Energy Efficiency Ratio (SEER)/ Seasonal Coefficient of Performance (SCOP) | Min 6.1/Min 4.6 |  |
| Energy saving Rank (Cooling/Heating) | Min A++/A++ |  |
| Refrigerant  | R410A |  |
| Input Power | 1F, 220 - 240 V, 50 Hz |  |
| Standard mounting and adjustment services (including consumables and additional services, like supports, pipes, ducts, cable, etc.) | Yes |  |
| 3 | **Type 3** | Split air conditioning system, wall mounted, inverter  |  |
| Reverse Cycle System (Cooling & Heating) | Yes |  |
| Other features  | Moisture removal, ventilation, auto |  |
| Cooling/Heating Capacity (BTU/h) | 12,000 BTU/12,000 BTU (20-30 m2 of office space) |  |
| Permissible Range of Outdoor Temp, ºC | Cooling: -10/+40; Heating: -10/+20 |  |
| Indoor/Outdoor Sound Level, dB | Max 35/60 |  |
| Seasonal Energy Efficiency Ratio (SEER)/ Seasonal Coefficient of Performance (SCOP) | Min 6.1/Min 4.6 |  |
| Energy saving Rank (Cooling/Heating) | Min A++/A++ |  |
| Refrigerant  | R410A |  |
| Input Power | 1F, 220 - 240 V, 50 Hz |  |
| Standard mounting and adjustment services (including consumables and additional services, like supports, pipes, ducts, cable, etc.) | Yes |  |
| 4 | **Type 4** | Split air conditioning system, wall mounted, inverter  |  |
| Reverse Cycle System (Cooling & Heating) | Yes |  |
| Other features  | Moisture removal, ventilation, auto |  |
| Cooling/Heating Capacity (BTU/h) | 9,000 BTU/9,000 BTU (10-20 m2 of office space) |  |
| Permissible Range of Outdoor Temp, ºC | Cooling: -10/+40; Heating: -10/+20 |  |
| Indoor/Outdoor Sound Level, dB | Max 35/60 |  |
| Seasonal Energy Efficiency Ratio (SEER)/ Seasonal Coefficient of Performance (SCOP) | Min 6.1/Min 4.6 |  |
| Energy saving Rank (Cooling/Heating) | Min A++/A++ |  |
| Refrigerant  | R410A |  |
| Input Power | 1F, 220 - 240 V, 50 Hz |  |
|  | Standard mounting and adjustment services (including consumables and additional services, like supports, pipes, ducts, cable, etc.) | Yes |  |