## SITE
REF: | ITB
Lot: | x | Solid biomass heating system and solar panels for hot water preparation in kindergarten no.2 of Cainari town, Causeni district
Site: | y
Consolidated price list |  |  |  | Estimated amount in USD, 0 rate VAT
Cost Component / Section
1 | Territory development |  |  | 0
2 | Thermomecanics |  |  | 0
3 | Solar hot water system |  |  | 0
4 | Heating and ventilation |  |  | 0
5 | General construction works |  |  | 0
6 | Electricity and lighting |  |  | 0
7 | Automated control and regulation system |  |  | 0
8 | Water and sewage |  |  | 0
9 | Anti fire system |  |  | 0
10 | Fuel system |  |  | 0
11 | Commissioning |  |  | 0
12 | Service and Maintenance works for 3-years of operation |  |  | 0
| Total price of works |  |  | 0
No | Parameter |  | Unit | Value
1 | Annual heat consumption |  | MWh | 513.47
2 | Boiler efficiency at nominal output |  | percentage | 0%
3 | Annual fuel demand |  | MWh
4 | Net calorific value of the fuel |  | MJ/ton | 15000
5 | Net calorific value of the fuel |  | MWh/ton | 4.1667
6 | Annual fuel consumption |  | ton
7 | Estimated fuel price |  | USD/ton | 110
8 | Annual cost of fuel |  | USD
9 | Discount rate |  | percentage | 10%
10 | Expected lifetime of the boiler |  | years | 10
11 | Current value (VC) of fuel |  | USD
Total cost of life-cycle (Price of works + VC fuel) |  |  | USD
Bidder: |  |  | Signature
No changes to the initial structure of this document are allowed. Any modifications made in the document, may result in Bidder's disqualification.

## TA
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solid biomass heating system and solar panels for hot water preparation in kindergarten no.2 of Cainari town, Causeni district
Site: | y
Section: |  | Territory development
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Construction works |  |  |  | 0
|  | Chapter 1.1. Concrete cement platform |  |  |  | 0
1 | DA06B2 | Layer of cylindrical natural aggregates, having the resistant function of filtering, isolation, ventilation, anti-freeze and proof course, with mechanical laying, with sand | m3 | 3.5 |  | 0
2 | DA06B1 | Layer of cylindrical natural aggregates, having the resistant function of filtering, isolation , ventilation, anti-freeze and proof course, with mechanical laying, with ballast | m3 | 3.5 |  | 0
3 | CG22A | Plain concrete flooring class C 10/8 (Bc 10/B 150) thickness 10 cm, in continuous surface, primed, poured on site, in rooms with surface bigger than 16 sqm (B25 (F200), gr.8 cm) | m2 | 35 |  | 0
4 | DE11A | Small curbs, ready-made from concrete with section 10x15 cm, to delimitate green areas, sidewalks, alleys, etc., placed on concrete foundation B-15, БР 100.20.8 | m | 20 |  | 0
|  | Chapter 1.2. Welded panels (Euro fence) - 37,50 m |  |  |  | 0
5 | CO06B correct | Fencing wire mesh with fence panels made of round steel frame fixed on ready-made reinforced concrete pillars mounted at 2 m distance from each other, interaxed by tamping the ballast, the ridge height of 1,80 m ("GARDLAIN") | m | 37.5 |  | 0
6 | CA03F | Plain concrete poured with classical means in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class В15 | m3 | 0.8 |  | 0
|  | Chapter 1.3. Gate "STANDART" l=1,0m, Н=1,8m (1 unit) |  |  |  | 0
7 | CK14A | Metallic gates with frames made of round steel profiles, ready-made, including the accessories necessary, mounted on reinforced concrete poles, gate STANDART code 6204 | m2 | 1.8 |  | 0
|  | Chapter 1.4. Metallic fence (9,60 m) |  |  |  | 0
8 | TsA02A | Manual digging of soil in limited spaces, under 1,00 m or over 1,00 m in width, executed without support, with vertical slope, in foundations, channels, drainages, twinning steps, in non-cohesive soil or lightly cohesive soil depth < 0,75 m light soil | m3 | 2.6 |  | 0
9 | TsD01B | Scattering with shovel of loose soil, in uniform layers, of 10-30 cm thickness, with a throw of up to 3 m from piles, including smashing the clods, soil from middle ground | m3 | 1.45 |  | 0
10 | TsD04B | Manual punning of piles made in horizontal or inclined digging at 1/4, including watering each soil layer in part with 10 cm thickness of cohesive soil | m3 | 1.45 |  | 0
11 | CO07C correct | Metallic fence of metal and tin frames of 1 mm thickness | kg | 392.98 |  | 0
14 | CA03F | Plain concrete poured with classical means in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according art. CA01, poured with classical means, plain concrete class В15 | m3 | 1.04 |  | 0
15 | TsC54B | Crushed stone foundation layer | m3 | 0.16 |  | 0
16 | CB02A | Boxes from reusable panels, with boarding from short and super short wood planks to pour the concrete in forms, glass-shaped foundations and equipment platforms including support | m2 | 10.24 |  | 0
|  | Chapter 1.5. Metallic gate (1 unit) |  |  |  | 0
17 | CO07C correct | Metallic fence of metal and tin frames of 1 mm thickness | kg | 27.95 |  | 0
18 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment | t | 0.03 |  | 0
19 | IzD04A | Painting the articles and metallic constructions with oil paint in 2 layers, executed from profiles, of 8mm-12mm thickness inclusive, with hand brush | t | 0.03 |  | 0
|  | Chapter 1.7. Steel ash containers Dn0,6х1,0(h) with lid - (6 units) |  |  |  | 0
23 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, all or partially embedded in concrete | kg | 336 |  | 0
24 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment | t | 0.336 |  | 0
25 | IzD04A | Painting the articles and metallic constructions with oil paint in 2 layers, executed from profiles, of 8mm-12mm thickness inclusive, with hand brush | t | 0.336 |  | 0
|  | Chapter 2. Equipment |  |  |  | 0
26 |  | Wheelbarrow with steel clamp, Vclamp=0,1m3 | un | 1 |  | 0
|  | Vertical systematization |  |  |  | 0
27 | TsA02B | Manual digging of soil in limited spaces, under 1,00 m or over 1,00 m in width, executed without support, with vertical slope, in foundations, channels, drainages, twinning steps, in non-cohesive soil or lightly cohesive soil depth < 0,75 m middle ground | m3 | 10 |  | 0
28 | RpCU09A | Manual transportation with wheelbarrow with rubber wheel at 100 m distance, the load of 100 - 120 kg, including setting the circulation cabinets and cleaning the rails of wheelbarrow by loading and unloading through settlement | t | 3.2 |  | 0
29 | TRI1AA04C3 | Loading materials from group A - light and small by throwing - from ramp or ground into vehicle of categ. 3 | t | 12.8 |  | 0
30 | TsI50A3 | Transport the soil with truck of 5t to 3km distance | t | 12.8 |  | 0
31 | TsD05B | Mechanical compacting with rammer of 150-200 kg of piles in successive layers of 20-30 cm thickness, excluding watering each layer in part, filling made of cohesive soil | 100 m3 | 0.02 |  | 0
|  | Demolition of buildings and installations |  |  |  | 0
32 | RpCB18F | Demolition of old concrete with mechanical means, plain concrete | m3 | 0.42 |  | 0
33 | RpCO56B | Dissembling: wainscoting and wood ceilings, plates, PFL, PAS, etc. | m2 | 26 |  | 0
34 | TRI1AA04C3 | Loading materials from group A - light and small by throwing - from ramp or ground into vehicle of categ. 3 | t | 1.25 |  | 0
35 | TsI50A3 | Transport the soil with truck of 5t to 3km distance | t | 1.25 |  | 0
Total VAT 0 rate | [5 empty] | 0

## TM
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solid biomass heating system and solar panels for hot water preparation in kindergarten no.2 of Cainari town, Causeni district
Site: | y
Section: |  | Thermomecanics
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Assembling works |  |  |  | 0
1 | IA14C | Monobloc steel heating boiler (hot water 90/70 degrees), with calorific power 150 kW | unit | 1 |  | 0
2 | IA14B | Monobloc steel heating boiler (hot water 90/70 degrees), with calorific power 100 kW | unit | 1 |  | 0
3 | IA38B | Circulating (recirculating) pump mounted on existing pipe, by flanges, with diameter over 2" | unit | 4 |  | 0
4 | IA28A | Expending vessel, mounted on platform having the capacity V=500 l | unit | 1 |  | 0
5 | IA25A | Pipe sludge separator, in central heating system, with nominal entering diameter 80 mm (dirt trap) | unit | 1 |  | 0
6 | IA38B | Circulating (recirculating) pump mounted on existing pipe, by flanges, with diameter over 2" | unit | 2 |  | 0
7 | IA23A | Liquid fuel filter (Dosaphos 250, Dn20 mm) | unit | 1 |  | 0
8 | IA38B | Circulating (recirculating) pump mounted on existing pipe, by flanges, with diameter over 2" | unit | 2 |  | 0
9 | IA17D | Vertical boiler mounted on floor, boiler having the capacity 3000 l (storage tank for heating system "SICC" 116Z) | unit | 1 |  | 0
10 | IA25A | Pipe sludge separator, in central heating system, with nominal entering diameter 20 mm (dirt trap) | unit | 2 |  | 0
11 | IA27B | Condenser reservoir, mounted on platform having the capacity 1000 l | unit | 1 |  | 0
12 | IA39A | Installation for water softeners, fully equipped, with water flow 900 -2250 l/h (Decalux-10 ET 500) | unit | 1 |  | 0
13 | ID03B | Three-way plug valve, with flanges with stuffing, for central heating installations, with nominal diameter 40 mm (Three-way plug valve VF3) | unit | 1 |  | 0
14 | SE58A | Heat meters with diameter -15 mm (Hydrometer) | unit | 1 |  | 0
|  | Chapter 2. Sanitary works |  |  |  | 0
15 | IzH05B | Pipe insulation with glass wool mattresses, mineral wool type I or type P stitched on one side, on weave of galvanized wire, made on site, having the thickness 60 mm, on pipes with circumference over thermal insulation more than 35 cm (mineral-cotton slabs with synthetic binder brand 75) | m2 | 13 |  | 0
16 | IzI09A1 | Protection of thermal insulation of black tin or galvanized pipes of 0,5 mm thickness screwed with round slot, self-tapping screws, having the circumference of pipe over thermal insulation between 0,90 and 1,6 m, manufacturing | m2 | 13.2 |  | 0
17 | IzI09A2 | Protection of thermal insulation of black tin or galvanized pipes of 0,5 mm thickness screwed with round slot, self-tapping screws, having the circumference of pipe over thermal insulation between 0,90 and 1,6 m, assembling | m2 | 13.2 |  | 0
18 | IzH40B | Insulation with perforated fiberglass cloth brand "ХПС-Т-5" of pipes of diameter over 25 mm | m2 | 13.27 |  | 0
19 | IzI09A1 | Protection of thermal insulation of black tin or galvanized pipes of 0,5 mm thickness screwed with round slot, self-tapping screws, having the circumference of pipe over thermal insulation between 0,90 and 1,6 m, manufacturing | m2 | 30.9 |  | 0
20 | IzI09A2 | Protection of thermal insulation of black tin or galvanized pipes of 0,5 mm thickness screwed with round slot, self-tapping screws, having the circumference of pipe over thermal insulation between 0,90 and 1,6 m, assembling | m2 | 30.9 |  | 0
21 | IzH05B | Pipe insulation with glass wool mattresses, mineral wool type I or type P stitched on one side, on weave of galvanized wire, made on site, having the thickness 40 mm, on pipes with circumference over thermal insulation more than 35 cm (mineral-cotton mats stitched in metal gauze lining type m2 brand 125) | m2 | 21.94 |  | 0
22 | IzI09A1 | Protection of thermal insulation of black tin or galvanized pipes of 0,5 mm thickness screwed with round slot, self-tapping screws, having the circumference of pipe over thermal insulation between 0,90 and 1,6 m, manufacturing | m2 | 24.9 |  | 0
23 | IzI09A2 | Protection of thermal insulation of black tin or galvanized pipes of 0,5 mm thickness screwed with round slot, self-tapping screws, having the circumference of pipe over thermal insulation between 0,90 and 1,6 m, assembling | m2 | 24.9 |  | 0
24 | CL16B | Thick sheet metal lining (silo funnels, chimney flues, tanks and troughs) in chimney flues (chimney flues) | t | 0.398 |  | 0
25 | IA18J | Fine fitting for central heating boilers: faucet control valve (for thermometer ЗКЧ-1-87) | unit | 7 |  | 0
26 | IA18J | Fine fitting for central heating boilers: faucet control valve (for pressure measuring ЗКЧ-275.00.90) | unit | 19 |  | 0
27 | IA18J | Fine fitting for central heating boilers: faucet control valve (for pressure measuring ЗКЧ-287.00.90) | unit | 12 |  | 0
28 | IA18J | Fine fitting for central heating boilers: faucet control valve (for measuring the level ЗКЧ-223-89) | unit | 2 |  | 0
29 | IA18J | Fine fitting for central heating boilers: faucet control valve (for measuring temperature ЗКЧ-2-87) | unit | 7 |  | 0
30 | ID04E | Stop or retaining valve with jacks for central heating installations, with nominal diameter 80 mm (ball valve JIP Standart FF "Danfoss") | unit | 2 |  | 0
31 | ID04F | Stop or retaining valve with jacks for central heating installations, with nominal diameter 80 mm (butterfly valve SYLAX (VFY-WH)) | unit | 14 |  | 0
32 | ID04D | Stop or retaining valve with jacks for central heating installations, with nominal diameter 65 mm (butterfly valve SYLAX (VFY-WH)) | unit | 4 |  | 0
33 | ID04B | Stop or retaining valve with jacks for central heating installations, with nominal diameter 40 mm (butterfly valve SYLAX (VFY-WH)) | unit | 2 |  | 0
34 | ID04B | Stop or retaining valve with jacks for central heating installations, with nominal diameter 32 mm (butterfly valve SYLAX (VFY-WH)) | unit | 2 |  | 0
35 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 25 mm (butterfly valve SYLAX (VFY-WH)) | unit | 4 |  | 0
36 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 20 mm (full-opening ball valve BVR UNI ISO 7/1) | unit | 11 |  | 0
37 | ID04E | Stop or retaining valve with jacks for central heating installations, with nominal diameter 80 mm (flange check valve type NVD402 "Danfoss") | unit | 4 |  | 0
38 | ID04B | Stop or retaining valve with jacks for central heating installations, with nominal diameter 40 mm (check valve type 223 "Danfoss") | unit | 1 |  | 0
39 | ID04B | Stop or retaining valve with jacks for central heating installations, with nominal diameter 32 mm (check valve type 223 "Danfoss") | unit | 1 |  | 0
40 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 20 mm (check valve type 223 "Danfoss") | unit | 2 |  | 0
41 | ID04B | Stop or retaining valve with jacks for central heating installations, with nominal diameter 40 mm (safety valve, full-opening, flange 17с29нж) | unit | 1 |  | 0
42 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 20 mm (safety valve, full-opening, flange 17с29нж) | unit | 4 |  | 0
43 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 15 mm (safety valve 17с29нж) | unit | 2 |  | 0
44 | ID06A | Air release valve with mobile key for central heating installations, with nominal diameter 10 mm (brass automatic air valve with threaded joining type MATIC company "Danfoss" VF3, 149 B5 106) | unit | 4 |  | 0
45 | ID06A | Air release valve with mobile key for central heating installations, with nominal diameter 10 mm (two-way safety valve Regulus DBV 1 3/4 Czech Rep) | unit | 2 |  | 0
46 | IC12D | Seamless or longitudinally welded steel pipe for constructions, welded in distribution pipelines, in central heating installations in residential or social-cultural buildings, pipe with outer diameter and wall thickness 89 x 3,0 mm | m | 45 |  | 0
47 | IC12C | Seamless or longitudinally welded steel pipe for constructions, welded in distribution pipelines, in central heating installations in residential or social-cultural buildings, pipe with outer diameter and wall thickness 76 x 3,0 mm | m | 7 |  | 0
48 | IC12A | Seamless or longitudinally welded steel pipe for constructions, welded in distribution pipelines, in central heating installations in residential or social-cultural buildings, pipe with outer diameter and wall thickness 57 x 3,0 mm | m | 15 |  | 0
49 | IC11E | Longitudinally welded black steel pipe for installations, non-threaded, welded in columns, in central heating installations in residential or social-cultural buildings, pipe having the diameter 45 x 2,8 mm | m | 7 |  | 0
50 | IC11D | Longitudinally welded black steel pipe for installations, non-threaded, welded in columns, in central heating installations in residential or social-cultural buildings, pipe having the diameter 38x2,8 mm | m | 5 |  | 0
51 | IC11D | Longitudinally welded black steel pipe for installations, non-threaded, welded in columns, in central heating installations in residential or social-cultural buildings, pipe having the diameter 32x2,8 mm | m | 15 |  | 0
52 | IC11C | Longitudinally welded black steel pipe for installations, non-threaded, welded in columns, in central heating installations in residential or social-cultural buildings, pipe having the diameter 25x2,8 mm | m | 37 |  | 0
53 | IC11B | Longitudinally welded black steel pipe for installations, non-threaded, welded in columns, in central heating installations in residential or social-cultural buildings, pipe having the diameter 20х2,0 mm | m | 1 |  | 0
54 | IE03D | Perform tightness test procedure under pressure of feeding pipelines of heating devices (heaters, thermal convectors, plinth convectors, etc.) with diameter 80 x 3,5 ... 159 x 8 mm | m | 45 |  | 0
55 | IE03C | Perform tightness test procedure under pressure of feeding pipelines of heating devices (heaters, thermal convectors, plinth convectors, etc.) with diameter 54 x 3,5 ... 83 x 3,5 mm | m | 22 |  | 0
56 | IE03B | Perform tightness test procedure under pressure of feeding pipelines of heating devices (heaters, thermal convectors, plinth convectors, etc.) with diameter 1 1/4" ... 2" | m | 27 |  | 0
57 | IE03A | Perform tightness test procedure under pressure of feeding pipelines of heating devices (heaters, thermal convectors, plinth convectors, etc.) with diameter 3/8" ... 1" | m | 38 |  | 0
58 | IE04D | Perform expansion-contraction and running test of pipes in heating installations heaters, (heaters, thermal convectors, plinth convectors, etc.) with diameter 89 x 3,5 ... 159 x 8 mm | m | 45 |  | 0
59 | IE04C | Perform expansion-contraction and running test of pipes in heating installations (heaters, thermal convectors, plinth convectors, etc.) with diameter 54 x 3,5 ... 83 x 3,5 mm | m | 22 |  | 0
60 | IE04B | Perform expansion-contraction and running test of pipes in heating installations heaters, thermal convectors, plinth convectors, etc.) with diameter 1 1/4" ... 2" | m | 27 |  | 0
61 | IE04A | Perform expansion-contraction and running test of pipes in heating installations heaters, thermal convectors, plinth convectors, etc.) with diameter 3/8" ... 1" | m | 38 |  | 0
62 | IC42A | Supports and fasteners for support of pipes, boilers, devices and recipients, having the weight less than 2 kg / unit | kg | 192.76 |  | 0
62A | Company price | Assembling manual valves, balancing, and commissioning of existing internal heating system integrated with newly assembled biomass heating system | system | 1 |  | 0
63 | VA05A | On-site assembling of ALP ventilation tubes, ready-made, having the section perimeter 450 mm (assembling the chimney) | m | 14 |  | 0
64 |  | Metal chimney with dual walls (made from stainless steel - for solid biofuel boilers) inner diameter 450 mm, H = 14,0 m, with thermal insulation - 50 mm, in set: |  |  |  | 0
65 |  | Stainless steel cone-shaped adaptor CF 450/520 | unit | 1 |  | 0
66 |  | Stainless steel wall clamp CFO-100 Д520 | unit | 6 |  | 0
67 |  | Stainless steel pipe CF L1000 Д450/520 | unit | 12 |  | 0
68 |  | Stainless steel condensation module CF Д450 | unit | 1 |  | 0
69 |  | Stainless steel lid module CF 87* Д520 | unit | 1 |  | 0
70 |  | Stainless steel tee CF 87* Д450/520 | unit | 1 |  | 0
|  | Chapter 3. Equipment |  |  |  | 0
71 |  | Monobloc steel heating boiler (hot water 90/70 degrees), with calorific power 150 kW with solid biofuel burning - pelettes, in set with control panel, productivity min 80%, Рnom = 1,5 bar, class 3, ЕН 303-5,2012 | unit | 1 |  | 0
72 |  | Monobloc steel heating boiler (hot water 90/70 degrees), with calorific power 100 kW with solid biofuel burning -pelettes, in set with control panel, productivity min 80%, Рnom = 1,5 bar, class 3, ЕН 303-5,2012 | unit | 1 |  | 0
73 |  | Circulating (recirculating) pump mounted on existing pipe, by flanges, with diameter over 2" (outlining No1), productivity Qp=10,8m3/hour, pressure Нр=6,7 m.c.a., N=22 -464 W, class А, А 16-2 (ЕЕ1<0,2) | unit | 2 |  | 0
74 |  | Circulating (recirculating) pump mounted on existing pipe, by flanges, with diameter over 2" (outlining No2), productivity Qp=10,8m3/hour, pressure Нр=15 m.c.a., N=30 -1336 W, class А, А 16-2 (ЕЕ1<0,2 | unit | 2 |  | 0
75 |  | Expending vessel V=500 l, , P=6 bar, 41VE0150 or similar | unit | 1 |  | 0
76 |  | Pipe sludge separator, in central heating system, with nominal entering diameter 80 mm (dirt trap), Р 16 bar, 149В 1802 or similar | unit | 1 |  | 0
77 |  | Circulating (recirculating) pump mounted on existing pipe, by flanges, with diameter over 2" Qp=1,6 m3/hour; Нр-4,5 m.c.a. N=37-96 W, MX 12-2 or similar | unit | 2 |  | 0
78 |  | Proportional water dosing equipment - build-in bypass oxygen D 20 mm, Dosaphos 250 or similar | unit | 1 |  | 0
79 |  | Water circulation pump, mounted on existing pipe, by flanges, with diameter over 2" Qp=0,1 m3/hour, pressure Нр=21,5 m.c.a., N=0,3 кW, BM1-3 or similar | unit | 2 |  | 0
80 |  | Vertical boiler (buffer) for heating system V=3000 L, Ру 8 bar | unit | 1 |  | 0
81 |  | Pipe sludge separator, in central heating system, with nominal entering diameter 20 mm (dirt trap), Р 16 bar, 149В 1769 or similar | unit | 2 |  | 0
82 |  | Vessel for additional water, V=1000 L | unit | 1 |  | 0
83 |  | Installation for water softeners, fully equipped, with water flow 900 -2250 l/h (Decalux-5 ET 500 or similar) | unit | 1 |  | 0
85 |  | Three-way plug valve, with flanges with stuffing, for central heating installations, with nominal diameter 40 mm, "Danfoss or similar" | unit | 1 |  | 0
86 |  | Heat meter D 15 mm, "Hydrometer" Sharky 775, h50-15), EN 1434 | unit | 1 |  | 0
Total VAT 0 rate | [5 empty] | 0

## TMS
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solid biomass heating system and solar panels for hot water preparation in kindergarten no.2 of Cainari town, Causeni district
Site: | y
Section: |  | Solar hot water system
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Assembling works |  |  |  | 0
1 | IA06M | Heat exchanger type B - 7 OL, delivered in 8 sections and mounted in 8 sections (vacuum solar collector APRICUS (30 tubes)) | unit | 4 |  | 0
2 | IA17B | Vertical boiler mounted on floor, boiler having the capacity 800 l (bivalent water heater) | unit | 1 |  | 0
3 | IA38B | Circulating (recirculating) pump mounted on existing pipe, by flanges, with diameter over 2" (GRUNDFOS, SOLAR 25-65 130 or similar) | unit | 1 |  | 0
4 | IA28A | Expending vessel, mounted on platform having the capacity 60 l, Maxivarem LR or similar | unit | 1 |  | 0
5 | IA17A | Vertical boiler mounted on floor, boiler having the capacity up to 25 l, inclusive (stainless steel drain back boiler) | unit | 1 |  | 0
6 | IA39A | Installation for water softeners, fully equipped, with water flow 900 -2250 l/h (ANTIKAL, MEDIUM 3/4 or similar) | unit | 2 |  | 0
7 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 20 mm (temperature blending valve) | unit | 1 |  | 0
8 | IA38B | Circulating (recirculating) pump mounted on existing pipe, by flanges, with diameter over 2" ("Biral", Primax15-6 130RED or similar) | unit | 4 |  | 0
|  | Chapter 2. Sanitary works |  |  |  | 0
9 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 15 mm (ball valve steel, with sockets Danfoss) | unit | 7 |  | 0
10 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 20 mm (ball valve steel, with sockets Danfoss) | unit | 15 |  | 0
11 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 20 mm (ball valve with brass filter) | unit | 1 |  | 0
12 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 20 mm (safety valve) | unit | 1 |  | 0
13 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 15 mm (safety valve) | unit | 1 |  | 0
14 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 20 mm (brass check valve with sockets) | unit | 5 |  | 0
15 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 15 mm (brass check valve with sockets) | unit | 2 |  | 0
16 | SE58A | Cold and hot water meter with diameter -20 mm (single jet water meter) | unit | 1 |  | 0
17 | IC31D | Copper pipe, welded, to connect heating devices and units, in central heating installations, with outer diameter 28,0x1,5 mm (in set with fittings TALOS) | m | 20 |  | 0
18 | IC31C | Copper pipe, welded, to connect heating devices and units, in central heating installations, with outer diameter 22,0x1,0 mm (in set with fittings TALOS) | m | 2 |  | 0
19 | IC11C | Longitudinally welded black steel pipe for installations, non-threaded, welded in columns, in central heating installations in residential or social-cultural buildings, pipe having the diameter 26,8x2,8 mm (iron-cast) | m | 22 |  | 0
20 | IC11B | Longitudinally welded black steel pipe for installations, non-threaded, welded in columns, in central heating installations in residential or social-cultural buildings, pipe having the diameter 21,3x2,8 mm (iron-cast) | m | 9 |  | 0
21 | RpIF09D | Insulation of pipes with special sleeves for insulation introduced in pipelines, with diameter and thickness from D=28x20 mm (thermal insulated pipe for high temperatures ARMAFLEX) | m | 20 |  | 0
22 | RpIF09D | Insulation of pipes with special sleeves for insulation introduced in pipelines, with diameter and thickness from D=22x20 mm (thermal insulated pipe for high temperatures ARMAFLEX) | m | 2 |  | 0
23 | VA05A | On-site assembling of ALP ventilation tubes, ready-made, having the section perimeter 80x2 mm (aluminium frilled tubular box ALUVENT) | m | 4 |  | 0
24 | IC42A | Supports and fasteners for support of pipes, boilers, devices and recipients, having the weight less than 2 kg / unit | kg | 9 |  | 0
25 | IzJ09B | Painting tin cover of pipelines and devices with oil pain in 2 layers, including priming | m2 | 1 |  | 0
|  | Chapter 3. Equipment |  |  |  | 0
26 |  | Vacuum solar collector APRICUS (30 pipes) in set with supports to mount on the roof APRICUS, ETC-30-Fn = 2,83 m2, Q = 2040W or similar | set | 4 |  | 0
27 |  | Mounting support | unit | 4 |  | 0
28 |  | Bivalent heater storage with indirect heat; V = 800 l, with build-in electronic element 380 V; Nel = 7,5 kW and temperature regulator TESY, EV12/9S2 800 or similar | set | 1 |  | 0
29 |  | Pumping block for solar collectors G = 1,6 m3 / h, H = 6,5 m, N = 6,5 m, N = 0,055 kW with debit meter and thermometer, GRUNDFOS, SOLAR 25-65 130 or similar | set | 1 |  | 0
30 |  | Expending vessel with diaphragm for hot wate V = 60 l; P = 6,0 bar Maxivarem LR or similar | set | 1 |  | 0
31 |  | Izolated stainless steel boiler, DRAIN BACK, for solar panel V = 25 l; P = 4,0 bar, with cooling agent for solar system, PROGALVA or similar | set | 1 |  | 0
32 |  | Anti-calcar magnetic device DN 20 mm, Q = 2,5 m3 / h, ANTIKAL, MEDIUM 3/4 or similar | set | 2 |  | 0
33 |  | Thermostatic mixing vent DN 20mm, 35-60 ° C, ESBE, VTA 322 35-60 ° C or similar | set | 1 |  | 0
34 |  | Hot water pump G = 1,1 m3 / h, H = 4,7 m, with electric engine, N = 0,003 ... 0,034 kW, EEN <0,15, "Biral", Primax15-6 130RED or similar | unit | 2 |  | 0
35 |  | Hot water recirculation pump G = 0,1 m3 / h, H = 6,0m, with electric engine N = 0,003 ... 0,034kW, EEN <0,15, "Biral", Primax15-6 130RED or similar | unit | 2 |  | 0
|  | Illumination and electrical lighting devices |  |  |  | 0
|  | Chapter 1. Assembling works |  |  |  | 0
36 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 6 |  | 0
37 | 08-03-530-4 | General magnetic starter, separated, mounted on wall or column, power up to 40 A ПmА-0247 | unit | 5 |  | 0
38 | 08-02-146-1 | Cable up to 35 kV, fixed with applied clamps, mass 1 m up to: 0,5 kg (ВВГнг(А)-LS-0,66 sect. 3х1,5 mm2) | 100 m | 0.75 |  | 0
39 | 08-02-146-1 | Cable up to 35 kV, fixed with applied clamps, mass 1 m up to: 0,5 kg (ВВГнг(А)-0,66 sect. 5х4 mm2) | 100 m | 0.12 |  | 0
40 |  | Cable with copper wires ВВГнг(A)-LS-0,66 sect. 3х1,5 mm2 | m | 75 |  | 0
41 |  | Cable with copper wires ВВГнг(A)-LS-0,66 sect. 5x4 mm2 | m | 12 |  | 0
|  | Chapter 2. Equipment |  |  |  | 0
42 |  | Automatic switch АД14/4/20/30 | unit | 1 |  | 0
43 |  | Automatic switch with three phases ВА47-29/1/С2 | unit | 5 |  | 0
44 |  | Contactor - ПmА-0247 Uн=220В | unit | 5 |  | 0
|  | Control and command system |  |  |  | 0
|  | Chapter 1. Assembling works |  |  |  | 0
45 | 11-02-002-01 | Device installed on flange combination, mass, kg, up to: 1,5 ТПГ100эк, ТmТБ | unit | 8 |  | 0
46 | 11-02-001-01 | Device installed on fillet combination, mass, kg, up to: 1,5 (controller) | unit | 1 |  | 0
47 |  | Control and warning panel ЩУС - box type ЯУЭ-1263 dim. 1200x600x350 |  |  |  | 0
48 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 4 |  | 0
49 | 11-08-001-04 | Connect the electric grid to devices by glue | 100 unit. | 0.8 |  | 0
50 | 08-02-148-1 | Cable up to 35 kV in posed pipes, blocks and boxes, mass 1 m up to: 1 kg | 100 m | 0.82 |  | 0
51 |  | Costs of materials |  |  |  | 0
52 |  | Selective device Г-16-225, В-16-225 | unit | 4 |  | 0
53 |  | Selective device Г-16-80, В-16-80 | unit | 8 |  | 0
54 |  | Metallic hosepipe D = 15mm | m | 10 |  | 0
55 |  | Control cable КВВГнг-LS sect. 4х1,5mm2 | m | 74 |  | 0
56 |  | Control cable КВВГнг-LS sect. 5х1,5mm2 | m | 8 |  | 0
|  | Chapter 2. Equipment |  |  |  | 0
57 |  | Thermometer ТПГ100эк-m1 | unit | 2 |  | 0
58 |  | Thermometer TMTБ41 | unit | 6 |  | 0
59 |  | Universal commutator УП5311 | unit | 3 |  | 0
60 |  | Chronometer ТЭ | unit | 1 |  | 0
61 |  | Supervisor EUROSTER-813 | unit | 1 |  | 0
Total VAT 0 rate | [5 empty] | 0

## HV
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solid biomass heating system and solar panels for hot water preparation in kindergarten no.2 of Cainari town, Causeni district
Site: | y
Section: |  | Heating and ventilation
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Heating |  |  |  | 0
1 | IB06C | Steel radiators, monobloc with length up to 1501 - 2000 mm ("Korado" type 33 1600х600(h) or similar) | unit | 1 |  | 0
2 | ID06A | Air release valve with mobile key for central heating installations, with nominal diameter 1/2" (straight locking valve RLV-15) | unit | 2 |  | 0
3 | ID06A | Air release valve with mobile key for central heating installations, with nominal diameter 1/2" (radiator's air release valve) | unit | 1 |  | 0
4 |  | Keys for air inlets R74Y001 | unit | 1 |  | 0
5 | ID06A | Air release valve with mobile key for central heating installations, with nominal diameter 15 mm (automatic air release valve R88IY003 Giacomini) | unit | 2 |  | 0
6 | ID04A | Stop or retaining valve with jacks for central heating installations, with nominal diameter 15 mm (ball valve drainage Giacomini) | unit | 1 |  | 0
7 | IC13A | Longitudinally welded black steel pipe, for installations, with thread and socket mounted by screwing the connections to devices in central heating installations, pipe with diameter 20x2,0 mm (electric welding) | m | 7 |  | 0
8 | IE03A | Perform tightness test procedure under pressure of feeding pipelines of heating devices (heaters, thermal convectors, plinth convectors, etc.) with diameter 3/8" ... 1" | m | 7 |  | 0
9 | IE04A | Perform expansion-contraction and running test of pipes in heating installations (heaters, thermal convectors, plinth convectors, etc.) with diameter 3/8" ... 1" | m | 7 |  | 0
10 | IzJ09B | Painting tin cover of pipelines and devices with oil pain in 2 layers, including priming | m2 | 0.91 |  | 0
11 | AcE51A | Connection to existing steel pipeline (with connecting pipes) with the diameter of connecting pipes 15 mm | part | 2 |  | 0
|  | Ventilation |  |  |  | 0
12 | VA02A | Manufacturing and mounting of straight ventilation channels, of galvanized steel or aluminium 0,3 - 2 mm thickness, having the perimeter of rectangular section 250 - 700 mm (gr.0,6 mm) | m2 | 3.92 |  | 0
13 | VB27A | Circular deflector with perimeter 230 - 700 mm (umbrella ЗKц-01 Д250) | unit | 1 |  | 0
14 | CC09B | Mounting rabbit mesh to support plaster ceiling , walls, protection of thermal insulators, masking of pipes, applied on straight ceilings, on steel - concrete D = 6-8 mm, with eyelids 26-35 mm inclusive | m2 | 0.15 |  | 0
15 | IzH05B | Pipe insulation with glass wool mattresses, mineral wool type I or type P stitched on one side, on weave of galvanized wire, made on site, having the thickness 20; 30; 40; 50 or 60 mm, on pipes with circumference over thermal insulation more than 30 mm (fiber optic mat, covered with armored aluminium foilgr.50 mm ISOVER-KIM-AL) | m2 | 5.5 |  | 0
16 |  | Adhesive band for sealing the joints ISOVER AL-TEPPI | m | 15 |  | 0
17 | CL20A | Ventilation grilles ready-made of black sheet, with manually adjustable blinds, painted and embedded in masonry (still air flowing grid SKP 500х300) | unit | 1 |  | 0
|  | Thermal networks |  |  |  | 0
18 | TsC03B1 | Mechanical digging with excavator of 0,40-0,70 mc, with internal combustion engine and hydraulic control, in soil with natural humidity, unloaded in piles on ground catg. II | 100 m3 | 0.29 |  | 0
19 | TsA20B | Manual digging of soil, in slopes, in channels cut by excavator or scraper, to fill the digging in slope profile, in middle ground | m3 | 1 |  | 0
20 | TsD02A1 | Scattering loose soil extracted from ground category I or II, by bulldozer tractor on tracks 65-80 CP, in layers of 15-20 cm | 100 m3 | 0.08 |  | 0
21 | TsD05A | Mechanical compacting with rammer of 150-200 kg of piles in successive layers of 20-30 cm thickness, excluding watering each layer in part, filling made of non-cohesive soil | 100 m3 | 0.08 |  | 0
22 | TsD01B | Scattering loose soil with spade, in uniform layers of 10-30 cm thickness, in a 3 m throw from pile, including breaking the clods, soil from middle ground | m3 | 2 |  | 0
23 | TsD04B | Manual punning of piles executed in horizontal or inclined digging at 1/4, including watering each layer of ground in part, having 10 cm thickness cohesive soil | m3 | 2 |  | 0
24 |  | Underground posing |  |  |  | 0
25 | TfA01B2 | Steel pipe installed in trench 1-3 m depth or on the ground at the height between 3-15m, including cold pressure testing, tightness testing and complex testing with circulating fluids, with diameter 89x3,0 mm | m | 28 |  | 0
26 | TfA01A2 | Steel pipe installed in trench 1-3 m depth or on the ground at the height between 3-15m, including cold pressure testing, tightness testing and complex testing with circulating fluids, with diameter 38х2,0 mm | m | 14 |  | 0
27 | TfA01A2 | Steel pipe installed in trench 1-3 m depth or on the ground at the height between 3-15m, including cold pressure testing, tightness testing and complex testing with circulating fluids, with diameter 32х2,0 mm | m | 49 |  | 0
28 | TfA02B2 | Ready-made steel elbow pipe, installed in the pipeline in trench 1-3 m depth or on the ground at the height of 3-15m, including cold pressure testing, tightness testing and complex testing with circulating fluids, with diameter 89 mm (pipe bend 90') | unit | 4 |  | 0
29 | TfA02B2 | Ready-made steel elbow pipe, installed in the pipeline in trench 1-3 m depth or on the ground at the height of 3-15m, including cold pressure testing, tightness testing and complex testing with circulating fluids, with diameter 89 mm (pipe bend 45') | unit | 4 |  | 0
30 | TfB02D2 | Assembling slide valve with vent or stop valve made of steel or iron up to Pn 40, in trench, 1-3 m depth or on the ground at the height up to 3-15m with nominal diameter Dn 80 mm (ball valve LD-WW) | unit | 2 |  | 0
31 | TfB02A2 | Assembling slide valve with vent or stop valve made of steel or iron up to Pn 40, in trench, 1-3 m depth or on the ground at the height up to 3-15m with nominal diameter Dn 32 mm (ball valve LD-WW) | unit | 1 |  | 0
32 | TfB02A2 | Assembling slide valve with vent or stop valve made of steel or iron up to Pn 40, in trench, 1-3 m depth or on the ground at the height up to 3-15m with nominal diameter Dn 25 mm (ball valve LD-WW) | unit | 9 |  | 0
33 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, fully or partially embedded in concrete | kg | 45.87 |  | 0
34 |  | Trench КЛ-90х45-8 (9 m) |  |  |  | 0
35 | TsC54A | Sand foundation layer | m3 | 1.22 |  | 0
36 | CP16A | Assembling L- or U-type elements made of reinforced concrete for trenches (thermal, heating, cables, etc.) hod Л6-8 | unit | 3 |  | 0
37 | CP16B | Assembling ready-made elements made of reinforced concrete for trenches (thermal, heating, cables, etc.), straight or curved plates П8-8 | unit | 3 |  | 0
38 | CP10B | Mount pre-cast elements from reinforced steel in residential and social-cultural buildings with monolith reinforced concrete structure, mixt or bearing masonry, at height up to 20 m including with volume from 0,2-2,5 mc bearing block ОП-1 | unit | 15 |  | 0
39 | CP10B | Mount pre-cast elements from reinforced steel in residential and social-cultural buildings with monolith reinforced concrete structure, mixt or bearing masonry, at height up to 20 m including with volume from 0,2-2,5 mc bearing block ОП-2 | unit | 8 |  | 0
40 |  | Pipe nozzle УТ 1 |  |  |  | 0
41 |  | Thermal chamber 1,8х2,4х2,0(h) |  |  |  | 0
42 | CP50A | Install ready-made concrete elements. Block-wall for basement, weight 0,5 t. Note: type of ready-made element is included accord. to project ФС-5m | unit | 4 |  | 0
43 | CP50A | Install ready-made concrete elements. Block-wall for basement, weight 0,5 t. Note: type of ready-made element is included accord. to project ФС-5-8m | unit | 12 |  | 0
44 | CP50A | Install ready-made concrete elements. Block-wall for basement, weight 0,5 t. Note: type of ready-made element is included accord. to project ФБС12.5.3-Т | unit | 6 |  | 0
45 | CP16B | Assembling ready-made elements made of reinforced concrete for trenches (thermal, heating, cables, etc.), straight or curved plates surface ПO-4 | unit | 2 |  | 0
46 | CA03F | Reinforced concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, reinforced concrete class.... B7,5 | m3 | 1.94 |  | 0
47 | CA03G | Reinforced concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, reinforced concrete class... В15, Фm-2в | m3 | 2.38 |  | 0
48 | CC01F | Concrete steel fittings OB 37 prepared in site workshop and mounted with bar diameter more than 8 mm including in continuous foundations | kg | 176.7 |  | 0
49 | CB02A | Boards from reusable panels, made from resinous short and super short boards to pour the concrete in forms, glass-shaped foundations and platforms for equipment including supports | m2 | 9.5 |  | 0
50 | AcE07A | Install steel or concrete steel lids on manholes of water and sewage systems, off road type I Т | unit | 2 |  | 0
51 | CP16B | Assembling ready-made elements made of reinforced concrete for trenches (thermal, heating, cables, etc.), straight or curved plates КЦО-1 | unit | 2 |  | 0
52 | CL10C | Metallic stairs, landings, bridges, bars and constructions to support technological equipment or metallic platforms for large aggregates delivered in ready-made sub-sets , at height up to 35 m, with weight up to 0,150 t, welded | t | 0.05 |  | 0
53 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment. | t | 0.05 |  | 0
54 | IzD04A | Painting the articles and metallic constructions with oil paint in 2 layers, executed from profiles, of 8mm-12mm thickness inclusive, with hand brush | t | 0.05 |  | 0
55 | CA03G | Reinforced concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, reinforced concrete class... B7,5, drainage pit and ДП-1 | m3 | 2.8 |  | 0
56 |  | Drainage pit ДК1 |  |  |  | 0
57 | AcE14A | Executing the manholes from ready-made reinforced concrete elements, for water supply circular (ring) for sewage with diameter 1,5 m, in soil without underground water | m3 | 1.99 |  | 0
58 | AcE14A1 | Ready-made reinforced concrete elements of manholes,circular (rig) with diameter 1,5 m, for sewage in soil without underground water. Note: resource with 0,00 (zero) norm is in accordance with the project | unit | 1 |  | 0
59 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment. | t | 0.03 |  | 0
60 | IzD04A | Painting the articles and metallic constructions with oil paint in 2 layers, executed from profiles, of 8mm-12mm thickness inclusive, with hand brush | t | 0.03 |  | 0
61 | CA02C | Plain concrete poured in equalizers, slopes at height up to 35 m inclusive, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class B7,5 | m3 | 0.97 |  | 0
62 | AcA16B | Install asbestos cement pipes assembled with steel sockets with flanges with the length 3 m and diameter 150 mm | m | 1.5 |  | 0
63 | TfB01H1 | Assembling slide valve with vent or stop valve made of steel or iron up to Pn 25, in trench, 1 m depth or up to 3 m high with nominal diameter Dn 150 mm (automatic stop valve) | unit | 1 |  | 0
64 |  | Mine ШО1, ШО2 (2 units) |  |  |  | 0
65 | CA03F | Reinforced concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, reinforced concrete class.... B15 | m3 | 2.84 |  | 0
66 | CA03F | Reinforced concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, reinforced concrete class.... B7,5 | m3 | 0.4 |  | 0
67 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, fully or partially embedded in concrete | kg | 50.12 |  | 0
68 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, fully or partially embedded in concrete | kg | 160 |  | 0
69 | DB16A | Asphalt concrete coat with small aggregates, executed at warm temperatures, in thickness of 2,5 cm manual laying | m2 | 4.2 |  | 0
70 | IzF04F | Hydro-insulated layer executed at temperature on terraces, roofs, or foundations on soils without underground waters, including mouldings of current hydro-insulation on inclined up to 40% or vertical, plane or curved surfaces, with bitumen or rubber bitumen applied with brush or rubber pump (purlin) lacquer БТ-577 | m2 | 4.2 |  | 0
71 | CC02E | Concrete steel fittings OB 37 prepared in site workshop, with bar diameter up to 8 mm inclusive, excluding constructions executed with sliding plates | kg | 3.4 |  | 0
72 | CC02F | Concrete steel fittings OB 37 prepared in site workshop, with bar diameter more than 8 mm, excluding constructions executed with sliding plates | kg | 10.56 |  | 0
73 |  | Nozzle "А" (4 unit) |  |  |  | 0
74 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, fully or partially embedded in concrete | kg | 4.8 |  | 0
75 | CE05A | Covers from anticorrosive profiled tin, curled or wrinkled, fixed with clamps, executed with dual stitches, executed on surfaces wider than 40 mp from profiled tin sheets of 0.4mm thickness, including execution of aprons, connection to chimneys etc. | m2 | 2.36 |  | 0
76 | IzF04F | Hydro-insulated layer executed at temperature on terraces, roofs, or foundations on soils without underground waters, including mouldings of current hydro-insulation on inclined up to 40% or vertical, plane or curved surfaces, with bitumen or rubber bitumen applied with brush or rubber pump (purlin) lacquer БТ-577 | m2 | 0.68 |  | 0
77 | IzH40B | Insulation with perforated fiberglass cloth brand "ХПС-Т-5" of pipes of diameter over 25 mm | m3 | 0.17 |  | 0
78 | IzH05B | Pipe insulation with glass wool mattresses, mineral wool type I or type P stitched on one side, on weave of galvanized wire, made on site, having the thickness 60 mm, on pipes with circumference over thermal insulation more than 35 cm (mineral-cotton slabs with synthetic binder brand 125 thickness50mm) | m2 | 12.4 |  | 0
79 | IzI05B | Thermo-insulation protection of pipes, executed with bitumen wire mesh type I A, tied with soft steel wire with diameter 1,25 mm РСТ | m2 | 25.5 |  | 0
81 | IzF04F k=2 | Hydro-insulated layer executed at temperature on terraces, roofs, or foundations on soils without underground waters, including mouldings of current hydro-insulation on inclined up to 40% or vertical, plane or curved surfaces, with bitumen or rubber bitumen applied with brush or rubber pump (purlin) 2 layers of cold bitumen | m2 | 14.4 |  | 0
82 |  | Aerial connection |  |  |  | 0
83 | TfA01B1 | Steel pipe installed in trench up to 1 m depth or up to 3 m high, including cold pressure testing, tightness testing and complex testing with circulating fluids, with diameter 89x3,0 mm | m | 30 |  | 0
84 | TfA01A1 | Steel pipe installed in trench up to 1 m depth or up to 3 m high, including cold pressure testing, tightness testing and complex testing with circulating fluids, with diameter 38x2,0 mm | m | 13 |  | 0
85 | TfA01A1 | Steel pipe installed in trench up to 1 m depth or up to 3 m high, including cold pressure testing, tightness testing and complex testing with circulating fluids, with diameter 32x2,0 mm | m | 13 |  | 0
86 | AcE51A | Connection to existing steel pipeline (with connecting pipes) with the diameter of connecting pipes 50 mm | part | 2 |  | 0
87 | TfA02B1 | Steel elbow pipe, ready-made, installed in trench up to 1 m depth or up to 3 m high, including cold pressure testing, tightness testing and complex testing with circulating fluids, with diameter 89 mm (pipe bend) | unit | 16 |  | 0
88 | TfA02B1 | Steel elbow pipe, ready-made, installed in trench up to 1 m depth or up to 3 m high, including cold pressure testing, tightness testing and complex testing with circulating fluids, with diameter 89х57 mm (transfer) | unit | 2 |  | 0
89 | TfB02D2 | Assembling slide valve with vent or stop valve made of steel or iron up to Pn 40, in trench, 1-3 m depth or on the ground at the height up to 3-15m with nominal diameter Dn 80 mm (ball valve LD-WW) | unit | 2 |  | 0
90 | TfB02A2 | Assembling slide valve with vent or stop valve made of steel or iron up to Pn 40, in trench, 1-3 m depth or on the ground at the height up to 3-15m with nominal diameter Dn 32 mm (ball valve LD-WW) | unit | 1 |  | 0
91 | TfB02A2 | Assembling slide valve with vent or stop valve made of steel or iron up to Pn 40, in trench, 1-3 m depth or on the ground at the height up to 3-15m with nominal diameter Dn 25 mm (ball valve LD-WW) | unit | 1 |  | 0
92 | TfB02A2 | Assembling slide valve with vent or stop valve made of steel or iron up to Pn 40, in trench, 1-3 m depth or on the ground at the height up to 3-15m with nominal diameter Dn 15 mm (ball valve LD-WW) | unit | 4 |  | 0
93 | IC44D | Manufacture, mounting and installation of safety pipe through masonry, pipe having the diameter 273 x 5,0 mm (L=0,5 m) | unit | 2 |  | 0
94 | IC44B | Manufacture, mounting and installation of safety pipe through masonry, pipe having the diameter 108x3,5 mm (L=0,5 m) | unit | 4 |  | 0
95 | IC44A | Manufacture, mounting and installation of safety pipe through masonry, pipe having the diameter 57х3,0 mm (L=0,5 m) | unit | 2 |  | 0
96 | IzH40B | Insulation with perforated fiberglass cloth brand "ХПС-Т-5" of pipes of diameter over 25 mm | m3 | 0.38 |  | 0
97 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, fully or partially embedded in concrete | kg | 0.56 |  | 0
98 | IC42A | Supports and fasteners for support of pipes, boilers, devices and recipients, having the weight less than 2 kg / unit | kg | 40 |  | 0
99 |  | Aerial assembling |  |  |  | 0
100 |  | Support ОП1(ОП2) |  |  |  | 0
101 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, fully or partially embedded in concrete | kg | 27.78 |  | 0
102 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment. | t | 0.03 |  | 0
103 | IzD04A | Painting the articles and metallic constructions with oil paint in 2 layers, executed from profiles, of 8mm-12mm thickness inclusive, with hand brush | t | 0.03 |  | 0
104 | CA03F | Plain concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, reinforced concrete class.... B15 | m3 | 0.36 |  | 0
105 | TsC54B | Broken stone foundation layer | m3 | 0.1 |  | 0
106 | IzH40B | Insulation with perforated fiberglass cloth brand "ХПС-Т-5" of pipes of diameter over 25 mm | m3 | 0.247 |  | 0
107 | IzH05B | Pipe insulation with glass wool mattresses, mineral wool type I or type P stitched on one side, on weave of galvanized wire, made on site, having the thickness 60 mm, on pipes with circumference over thermal insulation more than 35 cm (mineral-cotton slabs with synthetic binder brand 125 thickness50mm) | m2 | 13.2 |  | 0
108 | IzI09A1 | Protection of thermal insulation of black tin or galvanized pipes of 0,5 mm thickness screwed with round slot, self-tapping screws, having the circumference of pipe over thermal insulation between 0,90 and 1,6 m, manufacturing | m2 | 27.6 |  | 0
109 | IzI09A2 | Protection of thermal insulation of black tin or galvanized pipes of 0,5 mm thickness screwed with round slot, self-tapping screws, having the circumference of pipe over thermal insulation between 0,90 and 1,6 m, assembling | m2 | 27.6 |  | 0
110 | IzJ09B | Painting tin cover of pipelines and devices with oil pain in 2 layers, including priming | m2 | 12 |  | 0
111 |  | Dismantling and redo the asphaltic concrete |  |  |  | 0
112 | DG05A k=3 | Dismantle the coat up to 3 cm thickness, formed of permanent asphaltic coats, asphaltic concrete | m2 | 6 |  | 0
113 | DG01A | Dismantle the pavements or stone foundations on sand | m2 | 6 |  | 0
114 | TsC54A | Sand foundation layer | m3 | 0.9 |  | 0
115 | TsC54B | Broken stone foundation layer | m3 | 0.9 |  | 0
116 | DB16D k=2,5 | Asphalt concrete coat with small aggregates, executed at hot temperatures, in thickness de 4 cm manual laying (gr.10 cm) | m2 | 6 |  | 0
Total VAT 0 rate | [5 empty] | 0

## GCW
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solid biomass heating system and solar panels for hot water preparation in kindergarten no.2 of Cainari town, Causeni district
Site: | y
Section: |  | General construction works
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Ground works |  |  |  | 0
1 | TsC03B1 | Mechanical digging with excavator of 0,40-0,70 mc, with internal combustion engine and hydraulic control, in soil with natural humidity, unloaded in piles on ground catg. II | 100 m3 | 0.29 |  | 0
2 | TsA20B | Manual digging of soil, in slopes, in channels cut by excavator or scraper, to fill the digging in slope profile, in middle ground | m3 | 0.91 |  | 0
3 | TsD02A1 | Scattering loose soil extracted from ground category I or II, by bulldozer tractor on tracks 65-80 CP, in layers of 15-20 cm | 100 m3 | 0.12 |  | 0
4 | TsD01B | Scattering loose soil with spade, in uniform layers of 10-30 cm thickness, in a 3 m throw from pile, including breaking the clods, soil from middle ground | m3 | 2.93 |  | 0
5 | TsD04B | Manual punning of piles executed in horizontal or inclined digging at 1/4, including watering each layer of ground in part, having 10 cm thickness cohesive soil | m3 | 14.65 |  | 0
|  | Chapter 2. Foundation |  |  |  | 0
6 | TsC54B | Broken stone foundation layer | m3 | 1.65 |  | 0
7 | CA03F | Plain concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, reinforced concrete class.... (в/ц<0,55, B12,5) | m3 | 19.23 |  | 0
8 | CB02A | Boards from reusable panels, made from resinous short and super short boards to pour the concrete in forms, glass-shaped foundations and platforms for equipment including supports | m2 | 95.96 |  | 0
9 | IzF50A | Hydro-insulation made from cement mortar with liquid glass in foundations and walls applied on horizontal surfaces | m2 | 10.88 |  | 0
|  | Chapter 3. Wall |  |  |  | 0
10 | CD55A | Limestone masonry (block) in walls with height up to 4 m, plain masonry | m3 | 36.1 |  | 0
11 | CC03A | Assembling welded mesh at low height or equal to 35 m, in walls and diaphragms, with mesh weight up to 3 kg/mp СГ-1 | kg | 54 |  | 0
12 |  | Lintels Прm 1, Прm 2 |  |  |  | 0
13 | CA04F | Concrete poured in slabs, beams, pillars, prepared by concrete mixer or commercial concrete according to art. CA01 and pouring with classical means В15 | m3 | 0.44 |  | 0
14 | CC02K | Concrete steel fittings OB 37 prepared in site workshop, with bar diameter up to 8 mm inclusive, mounted in beams and poles at height less or equal to 35 m, excluding constructions executed with sliding plates | kg | 9.6 |  | 0
15 | CC02L | Concrete steel fittings OB 37 prepared in site workshop, with bar diameter more than 8 mm, and mounted in beams and poles at heights lower or equal to 35 m, excluding constructions executed with sliding plates | kg | 18.8 |  | 0
16 | CB02D | Boards from reusable panels, made from resinous short and super short boards to pour concrete in pillars and frames excluding supports at height up to 20 m inclusive | m2 | 3.64 |  | 0
17 | IC44B | Manufacture, mounting and installation of safety pipe through masonry, pipe having the diameter 108x2,8 mm (L=0,45 m) | unit | 2 |  | 0
18 | IC44C | Manufacture, mounting and installation of safety pipe through masonry, pipe having the diameter 152 x 2,8 mm (L=0,45 m) | unit | 2 |  | 0
19 | IC44D | Manufacture, mounting and installation of safety pipe through masonry, pipe having the diameter 219 x 3,0 mm (L=0,45 m) | unit | 2 |  | 0
|  | Chapter 4. Overlapping |  |  |  | 0
20 | CP53B | Floor tiles and cover for constructions, in areas with earthquakes 7-8 with support on 2 sides at the height of the building up to 35 m, with surface up to 10 m2 Note: type of ready-made element will be included according to project (1ПК61-10-4,5-С7) | unit | 7 |  | 0
21 |  | Belt Пm1 |  |  |  | 0
22 | CA04F | Concrete poured in slabs, beams, pillars, prepared by concrete mixer or commercial concrete according to art. CA01 and pouring with classical means В15 | m3 | 2.1 |  | 0
23 | CC02K | Concrete steel fittings OB 37 prepared in site workshop, with bar diameter up to 8 mm inclusive, mounted in beams and poles at height less or equal to 35 m, excluding constructions executed with sliding plates | kg | 31.9 |  | 0
24 | CC02L | Concrete steel fittings OB 37 prepared in site workshop, with bar diameter more than 8 mm, and mounted in beams and poles at heights lower or equal to 35 m, excluding constructions executed with sliding plates | kg | 177.8 |  | 0
25 | CB02C | Boards from reusable panels, made from resinous short and super short boards to pour concrete in plates and beams excluding supports at height up to 20 m inclusive | m2 | 12.55 |  | 0
26 | RpCU05F | Break stone or reinforced concrete walls to install pipes in walls of 16 -25 cm thickness | unit | 1 |  | 0
|  | Chapter 5. Roof |  |  |  | 0
27 | RpCU06C | Digging trenches of up to 5 cm depth, in stone or reinforced concrete walls 5 x 50 cm2 | m | 1.2 |  | 0
28 | CA04F | Concrete poured in slabs, beams, pillars, prepared by concrete mixer or commercial concrete according to art. CA01 and pouring with classical means В12,5 | m3 | 0.1 |  | 0
29 | CB02C | Boards from reusable panels, made from resinous short and super short boards to pour concrete in plates and beams excluding supports at height up to 20 m inclusive | m2 | 0.96 |  | 0
30 | CL57A | Assembling and fixing the elements embedded in monolith reinforced concrete: weight less than 4 kg | kg | 3.18 |  | 0
31 | CE17A | Additional ondutiss polymer layer mounted under the tile layer, corrugated or indented tiles (vapour barrier sheet) | m2 | 40.6 |  | 0
32 | IzF10F | Thermal insulation layer on terraces, roofs and flooring, made of mineral cotton type G 80 or G 100, made of mineral cotton type PIB, glued with bitumen on horizontal or inclined surfaces up to 40 % (mineral cotton Y=125 кг/m3, gr.150 mm) | m2 | 40.6 |  | 0
33 | CE17A | Additional ondutiss polymer layer mounted under the tile layer, corrugated or indented tiles (hydro insulation sheet) | m2 | 40.6 |  | 0
34 | IzF18B k=2 | Support layer of equalizer or protection for insulation, including related mouldings, executed with ready-made cement mortar brand M50-T without lime, plastered, on horizontal or inclined surfaces up to 40 % inclusiveg, applied in average thickness of 2 cm (4 cm thick) | m2 | 40.6 |  | 0
35 | CE41A | Treating the rafters with anti-septic | m3 | 1.59 |  | 0
36 | CN50A | Fire-proofing treatment of carpentry (arcs, beams, rafters, wall plates) | m3 | 1.59 |  | 0
37 | CE17A | Additional ondutiss polymer layer mounted under the tile layer, corrugated or indented tiles (condensation protection) | m2 | 92.4 |  | 0
38 | CE30B | Roof covering or tile covering, eternal type plates etc., from unprocessed resinous boards (24 mm thickness) sanded on one side, in ordinary constructions | m2 | 94.1 |  | 0
39 | CN51F | Antiseptic treatment of carpentry, on apparent surfaces with antiseptic: beams, wall plates. | 100m2 | 0.46 |  | 0
40 | CN50C | Fire-proofing of carpentry; mesh for covering and flooring. | 100m2 | 0.46 |  | 0
41 | CE40A | Mounting elements of beam frame (bars) with antiseptic treatment | m3 | 0.11 |  | 0
42 | CN50A | Fire-proofing treatment of carpentry (arcs, beams, rafters, wall plates) | m3 | 0.11 |  | 0
43 | CE31C | Clogged gutter, with apparent corbel, from soft resinous boards and sanded on one side, with average width 0,4 m | m2 | 20 |  | 0
44 | CN50A | Fire-proofing treatment of carpentry (arcs, beams, rafters, wall plates) | m3 | 0.45 |  | 0
45 | CN51B | Antiseptic treatment of carpentry, on hidden surfaces with antiseptic: timber frame. | m3 | 0.45 |  | 0
46 | CN16D | Painting with lacquers and oil paint applied on wood carpentry, executed in 2 layers of enamel paint on floors | m2 | 20 |  | 0
47 | CE06A | Covers from anticorrosive profiled tin, curled or wrinkled, mounted on metallic panels, executed on surfaces wider than 40 mp from profiled tin sheets connected with special clips or mechanical screws, of superior flange, including execution of aprons, connection to chimneys etc. (profiled sheet "LIDER" ЛК-20) | m2 | 94.1 |  | 0
48 | CE20A | Gutter systems brass type of anticorrosive protected tin Dn100 mm | m | 16.8 |  | 0
49 | CE22A | Pipe systems brass type of anticorrosive protected tin Dn100 mm | m | 16.4 |  | 0
50 | CE05B | Covers from anticorrosive profiled tin, curled or wrinkled, fixed with clamps, executed with dual stitches, executed on surfaces wider than 40 mp with tin sheets of 0,5 mm thickness, including execution of aprons, connection to chimneys etc (painted sheet "LIDER") | m2 | 20 |  | 0
51 | CK28B | Suspended ceilings executed on site of PFL or melamine PAL with plastic profiles (veneer) | m2 | 25.7 |  | 0
52 | IC43C | Manufacture, mounting and installation of safety pipe through panels, pipe having the diameter 133 x 3 mm (L=0,35 m) | unit | 1 |  | 0
53 | CL20A | Ventilation grilles ready-made of black sheet, with manually adjustable blinds, painted and embedded in masonry (blinds grid Жр-1, 780x580) | unit | 1 |  | 0
54 |  | Canopy К-1 |  |  |  | 0
55 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, fully or partially embedded in concrete | kg | 26.4 |  | 0
56 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment. | t | 0.03 |  | 0
57 | IzD04A | Painting the articles and metallic constructions with oil paint in 2 layers, executed from profiles, of 8mm-12mm thickness inclusive, with hand brush | t | 0.03 |  | 0
58 | CL57A | Assembling and fixing the elements embedded in monolith reinforced concrete: weight less than 4 kg | kg | 8.84 |  | 0
59 | CE06A | Covers from anticorrosive profiled tin, curled or wrinkled, mounted on metallic panels, executed on surfaces wider than 40 mp from profiled tin sheets connected with special clips or mechanical screws, of superior flange, including execution of aprons, connection to chimneys, etc. (profiled sheet "LIDER" ЛК-20) | m2 | 3.3 |  | 0
60 | CE05B | Covers from anticorrosive profiled tin, curled or wrinkled, fixed with clamps, executed with dual stitches, executed on surfaces wider than 40 sqm with tin sheets of 0,5 mm thickness, including execution of aprons, connection to chimneys etc (gr.0,8 mm) | m2 | 1.2 |  | 0
61 | CA05E | Concrete poured in straight walls, diaphragms, and different special constructions, situated above zero rate, at height up to 35 m including, prepared by concrete mixer or commercial concrete according to art.CA01 and pouring with classical means, reinforced concrete class... В15 | m3 | 0.14 |  | 0
|  | Chapter 6. Windows and doors |  |  |  | 0
62 | CK57D | Mounting PVC profiles: tilted (inclined, swing-out) with gap surface under 2 m2 in one frame | m2 | 5.08 |  | 0
63 | CK26A | Window sills installed at plastic windows, for windows and doors (PVC, b=250mm) | m | 2.4 |  | 0
64 | CK26B | Window sill installed on aluminium windows | m | 2.4 |  | 0
65 | CK12A | Metallic doors made from laminated steel profile, steel profiles prepared at cold temperatures, including fittings and accessories necessary to doors mounted in masonry of any nature in constructions with height up to 35 m including, in one frame, with surface sheath up to 7 sqm including (ИД-1) | m2 | 2.76 |  | 0
66 | CN20B | Internal or external painting on metallic carpentry with alkyd enamel in 2 layers including priming | m2 | 6.07 |  | 0
67 | CK25A | Doors made of plastic profiles including fittings and accessories necessary to doors mounted in masonry of any nature in constructions with height up to 35 m including, in one frame, with surface sheath up to 7 mp including (PVC, ИД-2) | m2 | 0.92 |  | 0
|  | Chapter 7. Floors |  |  |  | 0
68 | TsC53B | Compacting the ground with crushed stone | 100m2 | 0.41 |  | 0
69 | CG22A | Flooring made of plain concrete class C 10/8 (Bc 7,5/B 100) in thickness of 10 cm, in continuous surface, plastered, poured on site, in rooms with surface larger than 16 sqm | m2 | 40.6 |  | 0
70 | IzF03A1 | Anti-vapour barrier executed on horizontal surfaces with a layer of bitumen cardboard, glued on the entire surface with bitumen membrane | m2 | 40.6 |  | 0
71 | CG01A | Support layer for flooring executed from cement mortar M 150-T de 3 cm thickness with finely plastered surface (2 cm thick) | m2 | 40.6 |  | 0
72 | CG17D | Flooring from ceramic tiles including supporting layer of adhesive mortar, executed on surfaces: larger than 16 m2 (gr.13 mm) | m2 | 40.6 |  | 0
73 | CI14A | Linear ceramic tiles applied with adhesive | m | 24.35 |  | 0
|  | Chapter 8. Interior finishing |  |  |  | 0
74 | CF52B | Internal plastering of 5 mm thickness, manually executed, with dry mixture of plaster, on ceiling, manual preparation of mortar "Knauf" | m2 | 40.6 |  | 0
75 | CN53A | Priming of internal surfaces of walls and ceilings | m2 | 40.6 |  | 0
76 | CN01A | Plain painting with lime, made internally or externally on any support surface with two layers of lime | m2 | 40.6 |  | 0
77 | CF02B | Internal plastering of 2 cm thickness, plastered, manually executed, on walls or pillars, on flat surfaces with lime cement mortar brand M 100-T for spritz, prime and visible layer, on brick walls or small concrete blocks | m2 | 79.6 |  | 0
78 | CN53A | Priming of internal surfaces of walls and ceilings | m2 | 79.6 |  | 0
79 | CN06A | Interior painting with co-polymer vinyl in watering emulsion, applied in 2 layers on existing putty, manually executed | m2 | 79.6 |  | 0
|  | Chapter 9. External finishing |  |  |  | 0
81 | CF11A | External plastering sprayed on brick or concrete walls (with brush or pump) of 3 cm thickness, manually executed, with lime cement mortar M 50-T for spritz and lime cement mortar M 25-T for prime and visible layer in continuous surface | m2 | 14.1 |  | 0
82 | CF15A k=1,25 | External plastering, manually executed with cement mortar M 50-T of 2 cm average thickness on concrete or brick walls, with flat surfaces | m2 | 105.05 |  | 0
83 | CN54B | Manual application of primer with quartz "Gleta" in one layer on external walls | m2 | 105.05 |  | 0
84 | CF30A | External plastering de 2-3 mm. thickness, manually executed with "TINC" on walls | m2 | 105.05 |  | 0
|  | Chapter 10. Other works |  |  |  | 0
|  | Chapter 10.1. External stairs and ramp |  |  |  | 0
85 | TsA02B | Manual digging of soil in limited spaces, under 1,00 m or over 1,00 m in width, executed without support, with vertical slope, in foundations, channels, drainages, twinning steps, in non-cohesive soil or lightly cohesive soil depth < 0,75 m middle soil | m3 | 1.5 |  | 0
86 | TsD01B | Scattering loose soil with spade, in uniform layers of 10-30 cm thickness, in a 3 m throw from pile, including breaking the clods, soil from middle ground | m3 | 0.7 |  | 0
87 | TsD04B | Manual punning of piles executed in horizontal or inclined digging at 1/4, including watering each layer of ground in part, having 10 cm thickness cohesive soil | m3 | 0.7 |  | 0
88 | TsC54B | Broken stone foundation layer | m3 | 0.11 |  | 0
89 | CA03F | Plain concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, reinforced concrete class.... B7,5 | m3 | 1.1 |  | 0
90 | CB02A | Boards from reusable panels, made from resinous short and super short boards to pour the concrete in forms, glass-shaped foundations and platforms for equipment including supports | m2 | 7.75 |  | 0
91 | CG22A1 | Flooring made of plain concrete class C 10/8 (Bc 7,5/B 100) in thickness de 10 cm, in continuous surface, plastered, poured on site, in rooms with surface smaller or equal to 16 mp (В15, gr.2 cm) | m2 | 2.45 |  | 0
|  | Chapter 10.2. Foundations Фоm 1 ... Фоm 6 |  |  |  | 0
92 | TsC54B | Broken stone foundation layer | m3 | 0.93 |  | 0
93 | CA03G | Reinforced concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, reinforced concrete class... В12,5 | m3 | 2.29 |  | 0
94 | CC01C | Concrete steel fittings OB 37 prepared in site workshop and mounted with bar diameter up to 8 mm including in isolated foundations | kg | 8.2 |  | 0
95 | CC01D | Concrete steel fittings OB 37 prepared in site workshop and mounted with bar diameter more than 8 mm including in isolated foundations | kg | 48.4 |  | 0
96 | CL57A | Assembling and fixing the elements embedded in monolith reinforced concrete: weight less than 4 kg | kg | 70.61 |  | 0
97 | CB02A | Boards from reusable panels, made from resinous short and super short boards to pour the concrete in forms, glass-shaped foundations and platforms for equipment including supports | m2 | 8.8 |  | 0
|  | Chapter 10.3. Support ОП2 (13 units) |  |  |  | 0
98 | CL57A | Assembling and fixing the elements embedded in monolith reinforced concrete: weight less than 4 kg | kg | 26.39 |  | 0
99 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment. | t | 0.03 |  | 0
100 | IzD04A | Painting the articles and metallic constructions with oil paint in 2 layers, executed from profiles, of 8mm-12mm thickness inclusive, with hand brush | t | 0.03 |  | 0
|  | Chapter 10.4. Support ОП3 (1 unit), ОП4 (4 units) |  |  |  | 0
101 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, fully or partially embedded in concrete | kg | 20.11 |  | 0
102 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment. | t | 0.02 |  | 0
103 | IzD04A | Painting the articles and metallic constructions with oil paint in 2 layers, executed from profiles, of 8mm-12mm thickness inclusive, with hand brush | t | 0.02 |  | 0
104 | CA05E | Concrete poured in straight walls, diaphragms, and different special constructions, situated above zero rate, at height up to 35 m including, prepared by concrete mixer or commercial concrete according to art.CA01 and pouring with classical means, reinforced concrete class... В12,5 | m3 | 0.04 |  | 0
|  | Chapter 10.6. Metallic platform Пm1 (1 unit) |  |  |  | 0
108 | CL10C | Metallic stairs, landings, bridges, bars and constructions to support technological equipment or metallic platforms for large aggregates delivered in ready-made sub-sets , at height up to 35 m, with weight up to 0,150 t, welded | t | 0.26 |  | 0
109 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment. | t | 0.26 |  | 0
110 | IzD04A | Painting metallic articles and constructions with oil paint in 3 layers, executed from profiles with thickness between 8mm and 12mm including, with hand brush | t | 0.26 |  | 0
|  | Chapter 10.7. Chimney flue |  |  |  | 0
111 | TsA02B | Manual digging of soil in limited spaces, having under 1,00 m or over 1,00 m width, executed without support, with vertical slope, in foundations, channels, basements, twinning steps, in non-cohesive soil or lightly cohesive soil depth < 0,75 m middle ground | m3 | 9.8 |  | 0
112 | TsD01B | Scattering loose soil with spade, in uniform layers of 10-30 cm thickness, in a 3 m throw from pile, including breaking the clods, soil from middle ground | m3 | 5.65 |  | 0
113 | TsD04B | Manual punning of piles executed in horizontal or inclined digging at 1/4, including watering each layer of ground in part, having 10 cm thickness cohesive soil | m3 | 5.65 |  | 0
114 | CA02C | Plain concrete poured in equalizers, slopes at height up to 35 m including, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, plain concrete class B3,5 | m3 | 0.53 |  | 0
115 | CA03G | Reinforced concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, reinforced concrete class... В12,5 | m3 | 5.1 |  | 0
116 | CC01C | Concrete steel fittings OB 37 prepared in site workshop and mounted with bar diameter up to 8 mm including in isolated foundations | kg | 4.8 |  | 0
117 | CC01D | Concrete steel fittings OB 37 prepared in site workshop and mounted with bar diameter more than 8 mm including in isolated foundations | kg | 186.5 |  | 0
118 | CB02A | Boards from reusable panels, made from resinous short and super short boards to pour the concrete in forms, glass-shaped foundations and platforms for equipment including supports | m2 | 13.8 |  | 0
119 | CG01A | Support layer for flooring executed from cement mortar M 150-T of 3 cm thickness with finely plastered surface (5 cm thick) | m2 | 1.96 |  | 0
120 | CG01A1 k=4 | Support layer for flooring executed from cement mortar M 150-T of 3 cm thickness with finely plastered surface. The difference for each 0.5 cm of support layer of mortar M 150-T, should be added or deducted | m2 | 1.96 |  | 0
121 | CL18A | Various metallic structures made of laminated profiles, sheet, striated sheet, concrete, supporting or covering pipes, fully or partially embedded in concrete | tn | 1.33 |  | 0
122 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment. | t | 1.33 |  | 0
123 | IzD04A k=1.5 | Painting metallic articles and constructions with oil paint in 3 layers, executed from profiles with thickness between 8mm and 12mm including, with hand brush | t | 1.33 |  | 0
|  | Chapter 10.8. Dry wall |  |  |  | 0
124 | TsC54B | Broken stone foundation layer | m3 | 3.68 |  | 0
125 | CA02C | Plain concrete poured in equalizers, slopes, prepared by concrete mixer according to art. CA01 or commercial concrete, poured with classical means B12,5 | m3 | 2.57 |  | 0
Total VAT 0 rate | [5 empty] | 0

## EEF
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solid biomass heating system and solar panels for hot water preparation in kindergarten no.2 of Cainari town, Causeni district
Site: | y
Section: |  | Electricity and lighting
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Assembling works |  |  |  | 0
2 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 1 |  | 0
3 | 08-03-573-4 | Suspended cabinet (panel), height, width and depth, mm, up to (BZUM-TF-100-12) | unit | 1 |  | 0
4 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 2 |  | 0
5 | 08-03-600-2 | Meters mounted on prepared platform, three phases (ZMR110ACe) | unit | 1 |  | 0
6 | 08-03-573-4 | Suspended cabinet (panel), height, width and depth, 12 module box КmПн 2/12 IP55 | unit | 1 |  | 0
7 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 2 |  | 0
8 |  | Connector (connecting rail) YNS20-3-063 | unit | 2 |  | 0
9 |  | Connector (Rail) РЕ and N YNN10-14-100 | unit | 4 |  | 0
10 | 08-03-573-4 | Suspended cabinet (panel), 24 module box КmПн 2/24 ) IP55 | unit | 1 |  | 0
11 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 17 |  | 0
12 |  | Connecting rail YNS20-3-063 | unit | 2 |  | 0
13 |  | Rail РЕ and N YNN10-14-100 | unit | 4 |  | 0
14 | 08-03-573-4 | Suspended cabinet (panel), height, width and depth, (box К654У2) | unit | 1 |  | 0
15 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 1 |  | 0
16 |  | Plug socket with grounding contact IP54 | unit | 1 |  | 0
17 |  | Flexible cable КГ (А) LS 3х6 mm2 | m | 10 |  | 0
18 | 08-03-530-4 | General magnetic starter, separated, mounted on wall or column, power up to 40 A ПmА-0247 | unit | 8 |  | 0
19 | 08-03-603-1 | Box with descending transformers ЯТП-0,25-220/12 | unit | 1 |  | 0
20 | 08-03-594-2 | Source of light with luminescent light bulbs mounted separately on pivots, number of light bulbs, in Source of light, 2 ALS.OPL 218 IP54 | 100 unit | 0.04 |  | 0
21 | 08-03-594-2 | Source of light with luminescent light bulbs mounted separately on pivots, number of light bulbs, in Source of light, 2 СД 218 | 100 unit | 0.01 |  | 0
22 |  | Illuminating devices with fluorescent lights, ceiling ALS.OPL 218 IP54 | unit | 4 |  | 0
23 |  | Illuminating devices with fluorescent lights compact, ceiling CD 218 IP54 | unit | 1 |  | 0
24 |  | Torch СГВ-2 | unit | 1 |  | 0
25 |  | luminescent light bulbs ЛЛ-18 | unit | 8 |  | 0
26 |  | Compacted luminescent light bulbs ЛЛК-18 | unit | 2 |  | 0
27 | 08-03-591-2 | One button switch, open type, hidden. уIн=10А, Uн=220В IP43 | 100 unit | 0.02 |  | 0
28 | 08-03-591-8 | Plug socket open type, open switch socket | 100 unit | 0.02 |  | 0
29 | 08-02-472-3 | Earth binding conductor hidden in equalizer layer of floor, flat steel, section 100 mm2 (round steel) | 100 m | 0.3 |  | 0
30 | 08-02-471-4 | Earth plug, vertical, round steel, diameter 20 mm (round steel Д=20 mm) | 10 unit | 0.8 |  | 0
31 | 08-02-472-1 | Earth binding conductors: earth plug, horizontal, round steel, diameter 12 mm | 100 m | 0.7 |  | 0
32 | 08-02-146-1 | Cable up to 35 kV, fixed with applied clamps, mass 1 m up to: 0,5 kg (ВВГнг(А)-LS-0,66 sect. 3х1,5 mm2) | 100 m | 1.14 |  | 0
33 | 08-02-148-1 | Cable up to 35 kV in posed pipes, blocks and boxes, mass 1 m up to: 1 kg (ВВГнг(А)-LS-0,66 sect. 3х1,5 mm2) | 100 m | 0.24 |  | 0
34 | 08-02-146-1 | Cable up to 35 kV, fixed with applied clamps, mass 1 m up to: 0,5 kg (ВВГнг(А)-LS-0,66 sect. 3х2,5 mm2) | 100 m | 0.29 |  | 0
35 | 08-02-148-1 | Cable up to 35 kV in posed pipes, blocks and boxes, mass 1 m up to: 1 kg (ВВГнг(А)-LS-0,66 sect. 3х6 mm2) | 100 m | 0.02 |  | 0
36 | 08-02-146-1 | Cable up to 35 kV, fixed with applied clamps, mass 1 m up to: 0,5 kg (ВВГнг(А)-LS-0,66 sect. 3х6 mm2) | 100 m | 0.05 |  | 0
37 | 08-02-149-1 | Cable up to 35 kV suspended on steel cable, mass 1 m up to: 1 kg (ВВГнг(A)-LS sect. 5х10 mm2) | 100 m | 0.12 |  | 0
38 | 08-02-148-1 | Cable up to 35 kV in posed pipes, blocks and boxes, mass 1 m up to: 1 kg (ВВГнг(А)-LS-0,66 sect. 5х10 mm2) | 100 m | 0.43 |  | 0
39 | 08-02-146-1 | Cable up to 35 kV, fixed with applied clamps, mass 1 m up to: 0,5 kg (ВВГнг(А)-LS-0,66 sect. 5х10 mm2) | 100 m | 0.12 |  | 0
40 | 08-02-146-1 | Cable up to 35 kV, fixed with applied clamps, mass 1 m up to: 0,5 kg (ВВГнг(А)-FRLS-0,66 sect. .3x1,5 mm2) | 100 m | 0.06 |  | 0
41 |  | Cable with copper wires ВВГнг(A)-LS-0,66 sect. 3х1,5 mm2 | m | 138 |  | 0
42 |  | Cable with copper wires ВВГнг(A)-LS-0,66 sect. 3х2,5 mm2 | m | 29 |  | 0
|  | Cable with copper wires ВВГнг(A)-LS-0,66 sect. 3x6 mm2 | m | 7 |  | 0
43 |  | Cable with copper wires ВВГнг(A)-LS-0,66 sect. 5x10 mm2 | m | 67 |  | 0
44 |  | Cable with copper wires ВВГнг(A)-FRLS-0,66 sect. 3х1,5 mm2 | m | 6 |  | 0
45 | 08-02-407-6 | Steel pipe on constructions installed in primed channels executed, on flooring support, diameter up to 20 mm (steel pipe | 100 m | 0.17 |  | 0
46 | 08-02-411-1 | Metallic hosepipe, outer diameter up to 15 mm (metallic sleeve РЗ-ЦХ-Д20 mm) | 100 m | 0.09 |  | 0
47 | 10-06-034-14 | Different works: cable protection with plastic gutters, on brick or wood walls box 40х20 | m | 0.46 |  | 0
|  | Chapter 2. Sanitary works |  |  |  | 0
48 | 34-02-064-1 | Install support pillars for pair pipelines (tubular mast H=3,0m Dn40 mm) | unit | 2 |  | 0
49 | TsA02B | Manual digging of soil in limited spaces, having under 1,00 m or over 1,00 m width, executed without support, with vertical slope, in foundations, channels, basements, twinning steps, in non-cohesive soil or lightly cohesive soil depth < 0,75 m middle ground | m3 | 2.5 |  | 0
50 | TsD01B | Scattering loose soil with spade, in uniform layers of 10-30 cm thickness, in a 3 m throw from pile, including breaking the clods, soil from middle ground | m3 | 2.5 |  | 0
51 | TsD05B | Mechanical compacting with rammer of 150-200 kg of piles in successive layers of 20-30 cm thickness, excluding watering each layer in part, filling made of cohesive soil | 100 m3 | 0.025 |  | 0
|  | Chapter 3. Equipment |  |  |  | 0
52 |  | Automatic switch ВА47-29/3/С40 | unit | 1 |  | 0
54 |  | Control panel "BZUM-TF-100-12" | unit | 1 |  | 0
55 |  | Switch ВН 32-3Р/40 | unit | 1 |  | 0
56 |  | Automatic switch ВА47-29/3/С32 | unit | 1 |  | 0
57 |  | Active electric power meter ZCG 110ACe, Iн=5-60А, U=380В | unit | 1 |  | 0
58 |  | 12 module box КmПн 2/12 IP55 | unit | 1 |  | 0
59 |  | Switch ВН 32-3Р/32 | unit | 1 |  | 0
60 |  | Automatic switch one-way ВА47-29/1/С25 | unit | 1 |  | 0
61 |  | 24 module box КmПн 2/24 IP55 | unit | 1 |  | 0
62 |  | Commutator ПП-2P-25 | unit | 1 |  | 0
63 |  | Automatic switch one-way ВА47-29/1/C10 | unit | 2 |  | 0
64 |  | Automatic switch one-way ВА47-29/1/C6 | unit | 2 |  | 0
65 |  | Automatic switch one-way ВА47-29/1/С4 | unit | 5 |  | 0
66 |  | Automatic switch one-way ВА47-29/1/В4 | unit | 1 |  | 0
67 |  | Automatic switch one-way ВА47-29/1/С2 | unit | 4 |  | 0
68 |  | Automatic switch one-way ВА47-29/1/В2 | unit | 2 |  | 0
69 |  | Plug-in connector boxК654У2 | unit | 1 |  | 0
70 |  | Power switch ВН-32-1Р-25А | unit | 1 |  | 0
71 |  | Contactor - ПmА-0247 Uн=220В | unit | 8 |  | 0
72 |  | Mobile electric diesel generator 220V/50Hz, 6,0 кVA, equipped with automatic connection to electrical grid | unit | 1 |  | 0
Total VAT 0 rate | [5 empty] | 0

## ATM
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solid biomass heating system and solar panels for hot water preparation in kindergarten no.2 of Cainari town, Causeni district
Site: | y
Section: |  | Automated control and regulation system
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Assembling works |  |  |  | 0
1 | 11-02-002-01 | Device installed on flange combination, mass, kg, up to: 1,5 ТТУ, ТТП, ТПГ100эк | unit | 11 |  | 0
2 | 11-01-001-01 | Constructions for device installations, mass, kg, up to: 1 | unit | 9 |  | 0
3 | 11-02-001-01 | Device installed on fillet combination, mass, kg, up to: 1,5, (mП4, mВП, Дm2010) | unit | 43 |  | 0
4 | 11-02-001-01 | Device installed on fillet combination, mass, kg, up to: 1,5, (draft gauge ТНmП-52-m2) | unit | 1 |  | 0
5 | 11-02-001-01 | Device installed on fillet combination, mass, kg, up to: 1,5 (oxide detector RGD COO MP1) | unit | 1 |  | 0
6 | 11-02-001-01 | Device installed on fillet combination, mass, kg, up to: 1,5 (electronic regulator Danfoss) | unit | 1 |  | 0
7 | 10-08-003-01 | Warning siren CC-1 | unit | 1 |  | 0
8 | 11-03-001-01 | Devices, installed on metallic constructions, panels and console: device, mass, kg, up to: 5 (detection device РОС-301) | unit | 2 |  | 0
9 | 11-02-002-01 | Device installed on flange combination, mass, kg, up to: 1,5 detection device ESM-10 | unit | 1 |  | 0
10 | 11-02-002-01 | Device installed on flange combination, mass, kg, up to: 1,5 detection device EMSU-10 | unit | 1 |  | 0
11 | 11-01-001-01 | Constructions for device installations, mass, kg, up to: 1 (tap) | unit | 50 |  | 0
12 | 11-06-002-04 | Electrical grid through tubes in panels and consoles: steel tubes D=15mm | 100 m | 0.22 |  | 0
13 | 08-02-407-6 | Steel pipe on constructions installed in priming channels executed on flooring support, diameter up to 20 mm | 100 m | 0.07 |  | 0
14 | 11-08-002-01 | Connection of electrical grid through pipes to devices: water-gas pipelines, diameter of conventional section, up to 15 mm | 10 unit | 0.44 |  | 0
15 | 08-02-411-1 | Metallic hose, outer diameter up to 15 mm (РЗ-ЦХ-Ш15) | 100 m | 0.46 |  | 0
16 | 10-06-034-14 | Various works: cable protection with plastic covers on wood or brick walls | m | 40 |  | 0
17 | 08-02-148-1 | Cable up to 35 kV in posed pipes, blocks and boxes, mass 1 m up to: 1 kg | 100 m | 2.63 |  | 0
18 | 08-02-412-9 | Introduce conductors in posed metallic pipes and hoses: each following mono- or multi-wire conductor in general mesh, summary section up to 6 mm2 ПВ1-0,38 sec.1x1,5 mm2 | 100 m | 0.16 |  | 0
19 |  | Control and warning panel ЩУС - box type ЯУЭ-1263 dim. 1200x600x350 |  |  |  | 0
20 | 11-06-001-02 | Panel, mass, kg, up to: 100 / 1200х600х350 ЯУЭ1263 | unit | 1 |  | 0
21 | 08-03-575-1 | Device or equipment dissembled before transportation | unit | 86 |  | 0
22 | 11-08-001-04 | Connect the electric grid to devices by glue | 100 unit. | 1.6 |  | 0
23 |  | Costs of materials |  |  |  | 0
24 |  | Selection device Г-16-225, В-16-225 | unit | 19 |  | 0
25 |  | Selection device Г16-80, В-16-80, 955-2 | unit | 19 |  | 0
26 |  | Steel pipe D=15mm | m | 22 |  | 0
27 |  | Steel pipe D=20mm | m | 7 |  | 0
28 |  | Metallic hosepipe D=15mm | m | 36 |  | 0
29 |  | Cable trench | m | 40 |  | 0
30 |  | Cable КВВГнг-LS sect. 4х1,5mm2 | m | 146 |  | 0
31 |  | CableКВВГнг-LS sect. 5х1,5mm2 | m | 99 |  | 0
32 |  | Cable КВВГнг-LS sect. 7х1,5mm2 | m | 18 |  | 0
33 |  | Conductor ПВ1-0,38 sect. 1x1,5mm2 | m | 16 |  | 0
|  | Chapter 2. Equipment |  |  |  | 0
34 |  | Thermometer ТТУ, ТТП | unit | 9 |  | 0
35 |  | ThermometerТПГ100эк-m1 | unit | 2 |  | 0
36 |  | Relay sensor level РОС-301 | unit | 2 |  | 0
37 |  | Manometer mП4-У, mВП-Ух0,6 | unit | 35 |  | 0
38 |  | Manometer Дm2010Сr | unit | 8 |  | 0
39 |  | Detector CO RGD COOMP1 | unit | 1 |  | 0
40 |  | Warning siren СС-1 | unit | 1 |  | 0
41 |  | Electronic temperature regulator Danfoss | unit | 1 |  | 0
42 |  | Device to measure the volume ТНmП-52-m2 | unit | 1 |  | 0
43 |  | Control and command panel ЩУС-ЯУЭ-1263 1200x600x350mm IP54 | unit | 1 |  | 0
44 |  | Relay ПЭ37 | unit | 28 |  | 0
45 |  | Relay РСВ19-11 | unit | 5 |  | 0
46 |  | Relay РСВ19-31 | unit | 2 |  | 0
47 |  | Automatic switch ВА47-29/1/С2 | unit | 6 |  | 0
48 |  | Contactor УП5312 | unit | 10 |  | 0
49 |  | Contactor УП5311 | unit | 1 |  | 0
50 |  | Signalling device АD-22DS | unit | 13 |  | 0
51 |  | Diode Д246 | unit | 11 |  | 0
52 |  | Button ABLFS-22 | unit | 4 |  | 0
53 |  | Terminal block Бз24-4П | unit | 6 |  | 0
Total VAT 0 rate | [5 empty] | 0

## BK
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solid biomass heating system and solar panels for hot water preparation in kindergarten no.2 of Cainari town, Causeni district
Site: | y
Section: |  | Water and sewage
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | External water supply pipelines |  |  |  | 0
|  | Chapter 1. Assembling pipelines |  |  |  | 0
1 | TsC03B1 | Mechanical digging with excavator of 0,40-0,70 mc, with internal combustion engine and hydraulic control, in soil with natural humidity, unloaded in piles on ground catg. II | 100 m3 | 0.15 |  | 0
2 | TsA20B | Manual digging of soil, in slopes, in channels cut by excavator or scraper, to fill the digging in slope profile, in middle ground | m3 | 0.5 |  | 0
3 | TsD02A1 | Scattering loose soil extracted from ground category I or II, by bulldozer tractor on tracks 65-80 CP, in layers of 15-20 cm | 100 m3 | 0.11 |  | 0
4 | TsD05A | Mechanical compacting with rammer of 150-200 kg of piles in successive layers of 20-30 cm thickness, excluding watering each layer in part, filling made of non-cohesive soil | 100 m3 | 0.11 |  | 0
5 | TsD01B | Scattering loose soil with spade, in uniform layers of 10-30 cm thickness, in a 3 m throw from pile, including breaking the clods, soil from middle ground | m3 | 2.9 |  | 0
6 | TsD04B | Manual punning of piles executed in horizontal or inclined digging at 1/4, including watering each layer of ground in part, having 10 cm thickness cohesive soil | m3 | 2.9 |  | 0
7 | AcF03A | Filling the trenches for water and sewage pipelines, as sub-layer, protection layer, isolation layer or flange layer for drainage tubes, executed with sand | m3 | 0.96 |  | 0
8 | AcA52A | Polyethylene pipe, for water pipes embedded in trench, with diameter25 mm. Note: type of polyethylene pipe and warning band will be included according to the project PE80 SDR17,6 PN6 | m | 23 |  | 0
9 | AcF11C | Washing PVC, cast, cement, polyethylene pipes etc 20-75 mm, for drinking water after mounting and combining, before reception | m | 23 |  | 0
10 | AcF12A | Tightness test of polyethylene pipes mounted in trenches for water and sewage pipelines, with diameter up to 100 mm | m | 23 |  | 0
11 | AcB01A | Mounting fittings with manual or mechanical functioning (tubs, taps, vents), in water and sewage pipes, with diameter 15 mm (flange lock vent 15ч9р) | unit | 1 |  | 0
12 | AcA53A | Electrofusion mounting of fittings. Electr-fusion welding between polyethylene pipe and fitting (plugs, Tees, elbows)pipe with diameter 50x20 mm.Note: type of polyethylene fitting (plugs, Tees, elbows) will be included according to the project (saddle junction VALROM) | unit | 1 |  | 0
13 | AcA26A | Connecting the joint parts with flanges, flanges, including blind flanges and fittings, with diameter 15 mm (free flange) | unit | 2 |  | 0
14 | IC44B | Manufacture, mounting and installation of safety pipe through masonry, pipe having the diameter 89х3,7 mm (sleeve L=0,30 m) | unit | 1 |  | 0
15 | AcA10A | Assembling pressure polyethylene pipes in the ground, of high density for water supply, butt-welded, according to the norm I-6-PE, having the diameter 140 mm PE80 SDR17,6 PN6 | m | 13 |  | 0
16 | AcF13A | Treating the ends with bitumen and bitumen hemp at protection tubes with diameter: 150 mm | unit | 1 |  | 0
17 |  | Dismantling and redo the asphaltic concrete |  |  |  | 0
18 | DG05A k=3 | Dismantle the coat up to 3 cm thickness, formed of permanent asphaltic coats, asphaltic concrete | m2 | 4 |  | 0
19 | DG01A | Dismantle the pavements or stone foundations on sand | m2 | 4 |  | 0
20 | TsC54A | Sand foundation layer | m3 | 0.6 |  | 0
21 | TsC54B | Broken stone foundation layer | m3 | 0.6 |  | 0
22 | DB16D k=2,5 | Asphalt concrete coat with small aggregates, executed at hot temperatures, in thickness de 4 cm manual laying (gr.10 cm) | m2 | 4 |  | 0
|  | External sewage systems |  |  |  | 0
23 | TsC03B1 | Mechanical digging with excavator of 0,40-0,70 mc, with internal combustion engine and hydraulic control, in soil with natural humidity, unloaded in piles on ground catg. II | 100 m3 | 0.47 |  | 0
24 | TsA20B | Manual digging of soil, in slopes, in channels cut by excavator or scraper, to fill the digging in slope profile, in middle ground | m3 | 1.5 |  | 0
25 | TsD02A1 | Scattering loose soil extracted from ground category I or II, by bulldozer tractor on tracks 65-80 CP, in layers of 15-20 cm | 100 m3 | 0.31 |  | 0
26 | TsD05A | Mechanical compacting with rammer of 150-200 kg of piles in successive layers of 20-30 cm thickness, excluding watering each layer in part, filling made of non-cohesive soil | 100 m3 | 0.31 |  | 0
27 | TsD01B | Scattering loose soil with spade, in uniform layers of 10-30 cm thickness, in a 3 m throw from pile, including breaking the clods, soil from middle ground | m3 | 7.7 |  | 0
28 | TsD04B | Manual punning of piles executed in horizontal or inclined digging at 1/4, including watering each layer of ground in part, having 10 cm thickness cohesive soil | m3 | 7.7 |  | 0
29 | AcF03A | Filling the trenches for water and sewage pipelines, as sub-layer, protection layer, isolation layer or flange layer for drainage tubes, executed with sand | m3 | 2 |  | 0
30 | AcE15A | Executing the manholes from ready-made reinforced concrete elements, for water supply circular (ring) with diameter 2,0 m, in soil without underground water | m3 | 1.5 |  | 0
31 | AcE15A1 | Pre-cast reinforced concrete elements of manholes, circular (ring) with diameter 2,0 m, for sewage, in soil without underground water. Note: resource with 0.00 norm is in accordance with the project | unit | 1 |  | 0
32 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment. | t | 0.01 |  | 0
33 | IzD04A | Painting the articles and metallic constructions with oil paint in 2 layers, executed from profiles, of 8mm-12mm thickness inclusive, with hand brush | t | 0.01 |  | 0
34 | CD50A | Plain brick masonry, format 250 x 120 x 65 of external wall of height up to 4 m | m3 | 0.05 |  | 0
35 | TsC54B | Broken stone foundation layer | m3 | 0.31 |  | 0
36 | DB16A | Asphalt concrete coat with small aggregates, executed at cold temperatures, in thickness de 2,5 cm manual laying | m2 | 3.08 |  | 0
37 | AcE13A | Executing the manholes from ready-made reinforced concrete elements, for water supply circular (ring) with diameter 1,0 m, in soil without underground water | m3 | 1 |  | 0
38 | AcE13A1 | Pre-cast reinforced concrete elements of manholes, circular (ring) with diameter 1,0 m, for sewage, in soil without underground water. Note: resource with 0.00 norm is in accordance with the project | unit | 2 |  | 0
39 | IzD05A | Manual priming with one layer of minium lead paint on technological equipment. | t | 0.02 |  | 0
40 | IzD04A | Painting the articles and metallic constructions with oil paint in 2 layers, executed from profiles, of 8mm-12mm thickness inclusive, with hand brush | t | 0.02 |  | 0
41 | CD50A | Plain brick masonry, format 250 x 120 x 65 of external wall of height up to 4 m | m3 | 0.09 |  | 0
42 | TsC54B | Broken stone foundation layer | m3 | 0.62 |  | 0
43 | DB16A | Asphalt concrete coat with small aggregates, executed at cold temperatures, in thickness de 2,5 cm manual laying | m2 | 6.16 |  | 0
44 | AcA07B | Installing underground, outside buildings, the PVC pipes type 4(G) or 3(M), having the diameter 160 mm SN4 SDR41 | m | 26 |  | 0
45 | AcA07B | Installing underground, outside buildings, the PVC pipes type 4(G) or 3(M), having the diameter 110 mm SN4 SDR41 | m | 5 |  | 0
46 | RCsU05B | Drilling of plain concrete walls for pipes or ties up to 15 cm thickness | unit | 1 |  | 0
47 | RCsU07C | Matting the holes in plates with cement mortar after installation | unit | 1 |  | 0
48 |  | Dismantling and redo the asphaltic concrete |  |  |  | 0
49 | DG05A k=3 | Dismantle the coat up to 3 cm thickness, formed of permanent asphaltic coats, asphaltic concrete | m2 | 11 |  | 0
50 | DG01A | Dismantle the pavements or stone foundations on sand | m2 | 11 |  | 0
51 | TsC54A | Sand foundation layer | m3 | 1.65 |  | 0
52 | TsC54B | Broken stone foundation layer | m3 | 1.65 |  | 0
53 | DB16D k=2,5 | Asphalt concrete coat with small aggregates, executed at hot temperatures, in thickness de 4 cm manual laying (gr.10 cm) | m2 | 11 |  | 0
|  | Water pipeline |  |  |  | 0
|  | Chapter 1. Sanitary works |  |  |  | 0
54 | SF51A | Set to measure water debit without meter with pipe diameter 15 mm | set | 1 |  | 0
55 | SD19A | Straight stop valve with threaded sockets with diameter 15 mm (stop valve 15Б1бк) | unit | 1 |  | 0
56 | SD18A | Garden hosepipe installed in the ground with diameter 15 mm | set | 1 |  | 0
57 | SA01A | Galvanised steel pipe for installations installed in industrial constructions, having the diameter 15 mm | m | 6 |  | 0
58 | SF01A | Tightness test under pressure of hot or cold pipeline executed on steel, zinc pipelines, for installations, longitudinal welded, having the diameter 3/8"-2" | m | 6 |  | 0
59 | SF05A | Washing hot or cold water pipelines, executed from steel, zinc pipes, having the diameter 3/8"-2" | m | 6 |  | 0
60 | IzJ09B | Painting tin cover of pipelines and devices with oil pain in 2 layers, including priming | m2 | 0.36 |  | 0
61 | SD19A | Straight sop valve with threaded sockets with diameter 15 mm (tap) | unit | 1 |  | 0
62 | AcA52A | Polyethylene pipe, for water pipes embedded in trench, with diameter20 mm. Note: type of polyethylene pipe and warning band will be included according to the project PE80 SDR21 PN6 | m | 3 |  | 0
63 | TsA03E | Manual soil digging in limited spaces under 1m height made without supports, with inclined slope in foundations, trenches, etc. in middle or strongly cohesive soil, up to 1,5 m depth in middle ground | m3 | 1.4 |  | 0
64 | TsD01B | Scattering loose soil with spade, in uniform layers of 10-30 cm thickness, in a 3 m throw from pile, including breaking the clods, soil from middle ground | m3 | 1.4 |  | 0
65 | TsD04B | Manual punning of piles executed in horizontal or inclined digging at 1/4, including watering each layer of ground in part, having 10 cm thickness cohesive soil | m3 | 1.4 |  | 0
66 | CA03F | Reinforced concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, reinforced concrete class.... В7.5 | m3 | 0.06 |  | 0
|  | Chapter 2. Equipment |  |  |  | 0
67 |  | Cold water meter Dn15 mm | unit | 1 |  | 0
|  | Sewage pipeline |  |  |  | 0
68 | SB08E | Pipe from plastic material for sewage, connected with rubber set, mounted apparently or under the flooring, with diameter 100 mm polypropylene | m | 9 |  | 0
69 | SB08C | Pipe from plastic material for sewage, connected with rubber set, mounted apparently or under the flooring, with diameter 50 mm polypropylene | m | 19 |  | 0
70 | SF04A | Tightening and functioning test of sewage system made of cast tubes, for drainage, vynil polychrome pipe, non-plasticised, light or from plastic material, ductile iron having the diameter up to 100 mm inclusive | 10 m | 2.8 |  | 0
71 | SB08E | Pipe from plastic material for sewage, connected with rubber set, mounted apparently or under the flooring, with diameter 100 mm (polypropylene fittings 15%) | m | 1.35 |  | 0
72 | SB08C | Pipe from plastic material for sewage, connected with rubber set, mounted apparently or under the flooring, with diameter 50 mm (polypropylene fittings 15%) | m | 2.9 |  | 0
73 | SB10E | Connecting part (plain ramification) from plastic material for sewage, combined with rubber, with diameter 100 mm (polypropylene cleaning) | unit | 1 |  | 0
74 | SB10E | Connecting part (plain ramification) from plastic material for sewage, combined with rubber, with diameter 100 mm (polypropylene cleaning) | unit | 2 |  | 0
75 | SB24E | Simple, enamel steel floor drain, having the diameter 100 mm | unit | 1 |  | 0
76 | AcA25A | Connecting by welding the joining parts, steel, in position, having the diameter 100x50 mm (steel cone) | unit | 8 |  | 0
77 | SB10C | Connecting part (plain ramification) from plastic material for sewage, combined with rubber, with diameter 50 mm (clean drain) | unit | 8 |  | 0
78 | CA03F | Reinforced concrete poured with classical means, in foundations, basements, supporting walls, walls under zero rate, prepared by concrete mixer or commercial concrete according to art. CA01, poured with classical means, reinforced concrete class.... В7.5 | m3 | 0.24 |  | 0
79 | SA40A | Install anti-fire sockets on ceilings with panels (anti-fire sleeve) | unit | 1 |  | 0
80 | SC06A | Dripping cleanser (with one section), having a plastic drainage pipe, mounted on consoles fixed on brick walls | unit | 1 |  | 0
Total VAT 0 rate | [5 empty] | 0

## SIP
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solid biomass heating system and solar panels for hot water preparation in kindergarten no.2 of Cainari town, Causeni district
Site: | y
Section: |  | Anti fire system
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Chapter 1. Assembling works |  |  |  | 0
1 | 10-08-002-03 | Automatic alarm PC: thermal, smoke, light, protection against explosion ИП-105-2/1 | unit | 4 |  | 0
2 | 10-08-002-05 | Automatic OC alarm: crash, without electromagnetic or piezoelectric contact, installed on glass ИПР-2-01 | unit | 1 |  | 0
3 | 10-08-001-06 | Receiving devices: Devices "ПС" for reception and control, warning. Concentrator: 4 ways main block (Varta 1/2 GSM) | unit | 1 |  | 0
4 | 10-08-019-01 | Various electric clock equipment: Wall mounted ramification box | unit | 1 |  | 0
5 | 10-08-003-01 | Warning device with the capacity SA-913F | unit | 1 |  | 0
6 | 08-02-148-1 | Cable up to 35 kV in posed pipes, blocks and boxes, mass 1 m up to: 1 kg КПСЭСнг(А)-FRLS 2x2x0,2 | 100 m | 0.2 |  | 0
7 | 08-02-148-1 | Cable up to 35 kV in posed pipes, blocks and boxes, mass 1 m up to: 1 kg ВВГнг-FRLS sect. 2х1,5mm2 | 100 m | 0.06 |  | 0
8 | 08-01-121-1 | Stationary acid accumulator, type: С-1, СК-1 1270 ВАТТ | unit | 1 |  | 0
9 | 10-08-019-01 | Various electric clock equipment: Wall mounted ramification box УК-2П | unit | 2 |  | 0
10 | 10-06-034-14 | Various works: cable protection with plastic gutters, on wood or brick walls ТmК-1020 | m | 36 |  | 0
|  | Chapter 2. Equipment |  |  |  | 0
11 |  | Heat and fire detectors (10% reserve) ИП-105-2/1 | unit | 4 |  | 0
12 |  | Fire detectors ИПР-2-01 | unit | 1 |  | 0
13 |  | Fire signal reception device Varta 1/2 GSM | unit | 1 |  | 0
14 |  | Metalic Boc | unit | 1 |  | 0
15 |  | Alarm system with flashing lights 12В SA-913F | unit | 1 |  | 0
16 |  | Accumulator 12V7Ah | unit | 1 |  | 0
17 |  | Electrical pump to put down fires with refilling debit 36 m3/hour and vacuum depth 6 m, with hose pipe d=50mm and length 60m, mН-13/60 or similar | unit | 1 |  | 0
18 |  | Fire extinguisher ОП-5 | unit | 2 |  | 0
Total VAT 0 rate | [5 empty] | 0

## FSS
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solid biomass heating system and solar panels for hot water preparation in kindergarten no.2 of Cainari town, Causeni district
Site: | y
Section: |  | Fuel system
No. | Ref. code | Description of works | Unit of Measure | Quantity | Unit Price USD (wage inclusive) | Total USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
0
0
Total VAT 0 rate | [5 empty] | 0

## Commiss
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solid biomass heating system and solar panels for hot water preparation in kindergarten no.2 of Cainari town, Causeni district
Site: | y
Commissioning
№ | Item | Denumire lucrări | U.M. | Cantitate | Preţ unitar USD (inclusive salariu) | Total, USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
1 |  | Training of operators | curs | 1 |  | 0
2 |  | Measure the emissions | test | 1 |  | 0
3 |  | Measure performance indicators | test | 1 |  | 0
4 |  | Commissioning integral system | sistem | 1 |  | 0
Total fara TVA : | [5 empty] | 0
The bidder is responsible for any item that was not attributed a unit price and will be provided without additional costs for the UNDP

## Maintenance
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solid biomass heating system and solar panels for hot water preparation in kindergarten no.2 of Cainari town, Causeni district
Site: | y
Service and Maintenance works for 3-years of operation
№ | Item | Descrierea itemului | Periodicitatea | Cantitatea pentru 3 ani | Preţ unitar USD (inclusive salariu) | Total, USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
1 |  | Maintenance works and commissioning of heating system at the beginning of heating season | anual | 3 |  | 0
2 |  | Periodic maintenance works at the end of heating season | anual | 3 |  | 0
3 |  | Intervention and reparation of equipment in case of emergency | caz | 3 |  | 0
4 |  | Telephonic assistance in using the system | permanent | 1 |  | 0
Total fara TVA : | [5 empty] | 0
* Any equipment or component that requires replacement within the 3 years period and was not included in the list of wear parts shall be treated as a warranty case and must be provided by the contractor at no additional cost

## Boiler
- - bid for Lot: [x] Site: [y] - ref.: ITB
Lot: | x | Solid biomass heating system and solar panels for hot water preparation in kindergarten no.2 of Cainari town, Causeni district
Site: | y
Specificatiile minime ale cazanului
№ | Item | Specificatii cerute | Specificatiile propuse | Cantitate | Pret unitar USD | Total, USD (col.5 x col.6)
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | Cazan | Boiler model: |  | 2 | 1 | 2
Fuel type: agro-briquettes, type E, EN 14961-6 (according to Technical Specifications description) *
Limits of emission: EN 303-5:2012 Class 3
Q1= 100 kW, Q2= 150 kW**
Productivity: minimum 80% ****
Work pressure: ≥1.5 bar
Maximum admitted temperature at operation: ≥85 °C
Power tension: 230V/50Hz
Warranty for active components: 3 years
Warranty for passive components: 5 years
Burner cleaning: automatic cleaning system of burner through mechanical means
Diameter of smoke chimney mm 300mm***:
Capacity of fuel tank: VQ1= 510 L, VQ2=890 L
Boiler assembling scheme in existing boiler room in accordance with the normative in force *****
Total fara TVA : | [5 empty] | 2
* Specify type of fuel in accordance with the producer's recommendation
** Based on E type biofuel in accordance with theTechnical Specifications Description.
*** The bidder may suggest a boiler with higher or lower diameter than specified in project documentation, provided that the smoke chimney is compatible with the boiler and ensures its optimal operation, and the costs are adjusted accordingly in financial offer.
**** Specify only numerical value. Do not include text
***** The bidder will include an illustration to show the location of boilers in the boiler room by indicating main dimensions