## Sheet1
WHO ITB 2021/EURO/MDA/0016
Annex 1. Detailed List of requirements and specifications
# | Item | Technical specification | Unit | Quantity
LOT No. 1. Vaccine cooling systems
1 | Walk-in Cold Room | Capacity (m3): 30; Dimensions approx. (W x D x H mm): 4500 x 3600 x 2300; Wall & ceiling panel finish: Polyester coated steel or corrosion-resistant material or stainless steel or zinc coated steel; Doors must be lockable with 100% fail-safe provision for opening from inside. The clear opening width of the door must be 800mm min.um; Panel insulation material: Polyurethane high density; the average thermal transmittance (U value) of the roof, wall and floor panels, including joints, must be 0.17 W/m²K or better; Provide an internal clear plastic strip curtain. Provide a door frame heating element Panel insulation thickness options (mm): 100 mm (standard); Panel connection system: Cam-lock; Floor panel finish: anti-slip; Shelve mounting: Wall / Self-standing; Shelving system: Fully adjustable; Shelving material: Hygienic plastic; Refrige. Units options: Dual refrigeration units -monobloc system or weatherproof split system; All units should be fitted with run-hour meters.; Duty sharing: Automatic; Other frige options: Plume guard, Pressure relief valve, Cold climate protection, Auto-defrost, Strip curtain, Surge protection, Alarm system; Internal Temp. Range (˚C): +2…+8; Ambient temp. (˚C) Max.: +43; Power Supply: 220/380V, 50Hz; The thermostat must be calibrated to ITS-90 and be accurate to ± 0.5°C or better. Warranty min.: 1 year; Installation: should be included. Refrigerant: CFC-free to comply with the requirements of the Montreal Protocol. Cold room to be connected to both the main grid power supply and to a standby generator Cold room must be accompanied by a comprehensive package of printed instruction material Training: Provide a practical hands-on training course for users and/or maintenance technicians Qualification: Installation qualification and commissioning of installationsa according to PQS Verification Protocol E001/CR-FR01-VP2.4 | pcs | 2
2 | Walk-in Cold Room (Edinet, Balti, Cahul, UTA Gagauzia, Transnistria) | Capacity (m3): 10; Dimensions approx. (W x D x H mm): 2000 x 2000 x 2600; Wall & ceiling panel finish: Polyester coated steel or corrosion-resistant material or stainless steel or zinc coated steel;; Doors must be lockable with 100% fail-safe provision for opening from inside. The clear opening width of the door must be 800mm min.um; Panel insulation material: Polyurethane high density; the average thermal transmittance (U value) of the roof, wall and floor panels, including joints, must be 0.17 W/m²K or better; Provide an internal clear plastic strip curtain. Provide a door frame heating element Panel insulation thickness options (mm): 100 mm (standard); Panel connection system: Cam-lock; Floor panel finish: anti-slip; Shelve mounting: Wall / Self-standing; Shelving system: Fully adjustable; Shelving material: Hygienic plastic; Refrige. Units options: Dual refrigeration units -monobloc system or weatherproof split system; All units should be fitted with run-hour meters.; Duty sharing: Automatic; Other frige options: Plume guard, Pressure relief valve, Cold climate protection, Auto-defrost, Strip curtain, Surge protection, Alarm system; Internal Temp. Range (˚C): +2…+8; Ambient temp. (˚C) Max.: +43; Power Supply: 220/380V, 50Hz; The thermostat must be calibrated to ITS-90 and be accurate to ± 0.5°C or better. Warranty min.: 1 year; Installation: should be included. Refrigerant: CFC-free to comply with the requirements of the Montreal Protocol. Cold room to be connected to both the main grid power supply and to a standby generator Cold room must be accompanied by a comprehensive package of printed instruction material Training: Provide a practical hands-on training course for users and/or maintenance technicians Qualification: Installation qualification and commissioning of installationsa according to PQS Verification Protocol E001/CR-FR01-VP2.4 | pcs | 5
3 | Refrigerator (for LAB consumables) | Temperature Range: °C +2 to +8; Uniformity in performance, (AMB 20°C), °C: 2,0; Defrost: automatic; Internal air distribution: Air Stream; Number of compressors: 1; Voltage, V 220 – 240, Hz 50/60; Gross volume, litres (cu. ft.) 357 (12,6) Net volume, litres (cu. ft.) 214 (7,55) Inner Height, Width Depth mm approx. 1492, 495, 443; Certifications/Standards: 93/42/EEC, Class I; Shelfs: Standard; Shelfs material: Steinless steel; Number of shelfs incl bottom shelf: 5; Other options: Lock, LED light, Porthole Yes, Contact for remote alarm, Castors, Solid Doors. | pcs | 4
4 | Vaccine/Waterpack freezer | Temperature range, at 43°C: AMB-18 to -28; Energy source: 220-240V 50/60Hz; Icepack storage capacity: litres256 x 0.6; Icepack freezing capacity: kg/24 hrs.7.2; Gross volume: approx.: 281 L; Ext dimensions (HxLxD) approx.: 84 x 156 x 70 cm; Waterpack freezing capacity: 7.2 kg/24h, 256 x 0.6 L; Ambient operating temperature: Max. +43°C; Fuel and cycle type: Electric – compression; Climate zone: Hot; Supplied with: Temperature Monitoring Device, Lid with lock (2 keys); No. of baskets: 3. | pcs | 1
5 | Temperature and failure monitoring system for refrigerators | Unified central control and monitoring unit with connection to refrigerators/freezers controllers; GSM module; Instalation of the system should monitor the national warehouse and 5 subnational warehouse (public health centers warehouses) Visualization and alarm software, displays the following information: sensor readings, emergency messages, the functional state of the refrigeration equipment with measurement, possibility to store the recorded information throughout the calendar year, transmission messages to mobile phone; Tempreature sensors accuracy ±0.5°C or better,; Door open sensors; Base station; Instalation included in the price; Cost of the equipment included in the price; PQS performance specification, WHO/PQS/E006/TR03.2 3 units Vehicle Monitoring service: EDGE / GPRS / GSM network support and tempreture monitoring; Mobile device with localization signals from GPS satellites and transmition to Control Center via EDGE / GPRS or GSM network; Control Center: vehicle monitoring service provider; | pcs | 1
LOT No. 2. IT equipment
1 | Barcode printer | Resolution: 12 dots/mm (300 DPI); Print speed: up to 152 mm/second; Print width: up to 106 mm; Print length: up to 11,430 mm (450") 2,540 mm (100") Printing method Thermal Transfer & Direct Thermal; LCD/LED: LCD/LED panel with 8 big icons; SDRAM: min 128 MB; Flash min 128 MB; Extension: microSD card reader for Flash memory expansion; Ribbon capacity: 300 m long; Interface: USB port; RS-232; Ethernet; 10/100 Mbps; USB Host; (slot-in) 802.11 a/b/g/n Wi-Fi; Software support: SAP, Oracle, WHQL 8.1, Windows, Linux, MAC X.10, Mircosoft SQL Server. | pcs | 2
2 | Supplies for Barcode printer | for 6 months of working, using resource:1000 labels per working day; | set | 2
3 | Wireless 2D scanner | 1 MP optics for high quality scanning; High quality technology with highly visible white-illumination and 4-Dot aimer with center cross for targeted scanning; Motion-sensing technology for seamless reading mode transitions; Omnidirectional reading; Image capture and document scanning capabilities; Reads 1D, 2D, postal codes, stacked and composite bar codes and dot codes; Digital Watermarking and DPM reading on specific models/applications; Choice of Bluetooth wireless technology version 4.0 with BLE or Cordless System (radio frequencies available in 433 MHz or 910 MHz); Wireless battery charging system; Adjustable position cradle with Scan-While- Charging capability; Batch Mode capability; Point-to-point / Point-to-multipoint transmission; Long lasting user-replaceable Lithium-Ion battery. | pcs | 12
4 | Desktop computer with monitor and accessories | System Unit: min. 4 Cores Threads: min. 12MB Processor base frequency: min. 2.4 GHz TDP: min. 35W RAM: min. 8GB Memory type: DDR4, M.2 Memory: min. 256GB SSD WiFi no ODD Adapter; Monitor: min. 23" IPS/LED, (min. 4ms, min. 100M:1, min. 250cd, min. 1920x1080, 178°/178°, VGA, HDMI, Audio Line-out); USB mouse; USB Keyboard; HD Video Webcam, 720p HD Webcam with convenient built-in microphone, 1,43m, USB; Sourge protector extention cord. | set | 41
5 | Multifunction Unit (Print, Copy, and Scan) | MFD Colour Print/Scan/Copier/ Wi-Fi+Cloud Link, A4, ESAT; Print 4800x1200dpi, Scan 600x1200dpi, 64-275 g/м2, Paper Input: min 50 sheets, USB, Wi-Fi, Display LCD, CMY/CMYC | pcs | 41