## Sheet1
WHO ITB 2021/EURO/MDA/0017
Procurement of backup power supply (diesel generator) for the needs of the National Vaccine Warehouse of the Republic of Moldova
Annex 4. Bidder's offer
# | Item | Technical requirements | Technical specification proposed by Bidder | Unit | Quantity | Unit price, USD | Amount, USD VAT exclusive | Earliest Delivery date | Comments
1 | Diesel genarator | Engine type: diesel; Power, maximum: 175-180KVA; 140-150 KW; Power, nominal: 159-165 KVA; 127-130 KW; Reservoar capasity: min 300 litres; Engine Speed, rpm, approx.: 1500; Output Voltage, V: 400/230; Noise: max. 78 dB; Governor Type: Mechanic/Electronic; Aspiration: Turbocharge, Intercooler; Injection Type: Direct Injection; Cooling System: Liquid Cooled; Battery Capacity: 2x60 min; Frequency, Hz: 50; Automatic Voltage Regulation; Phases: 3; Overload: 1 Hour %110; Warning System: Self Alert; Connecting Type: Star or other compatible; Protection Class: IP 23; Isolation Class: H. |  | pcs | 1 | 0 | 0
2 | Warranty and maintenance | To be included in the price of item No.1 |  | months | 12 | 0 | 0
3 | Staff briefing | To be included in the price of item No.1 |  | hours | 3 | 0 | 0
TOTAL | [5 empty] | 0 | 0